## Instructions
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | Green Star Rulings*
x | x | x | x | x | x | x | x | *previously called Technical Clarifications and Credit Interpretation Request Spreadsheet
x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | The Green Building Council of Australia (GBCA) requests that this document be used in conjunction with the relevant Green Star Technical Manual. To obtain a copy, please see www.gbca.org.au.
x | x | x | x | x | x | x | x | How to Use This Spreadsheet
x | x | x | x | x | x | x | x
x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | Start by selecting the rating tool on the ‘Selection’ worksheet. Wait a few moments as the macros run. When the spreadsheet is ready to use, you will see the Changelog appear. To find your desired technical clarification or CIR ruling, click on the worksheet corresponding to the Green Star category or credit. To switch to another rating tool, simply return to the Selection Tab and click on another tool.
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | Q: ‘Why do I receive an error when I open the spreadsheet’
x | x | x | x | x | x | x | x
x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | Macros must be enabled for the spreadsheet to operate properly. If an error message pops up when you open the spreadsheet, please follow the help tips provided by Excel. Errors commonly result from Macro security settings being set too high. If your Macro security settings are set to High or Very High, change this to Medium by following Excel’s instructions below:
x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x | x x x x x x x x x x |  | 1. Select the Tools menu option and then select Macro and Security. In the resulting Security dialog, set the security level to Medium by clicking the Medium radio button. 2. Close the file and any other instances of the application currently running on the computer (close all applications that also use the application you are currently running). 3. Open the file again and examine the certificate of trust details and set the Always trust macros from this publisher box if you trust the certificate issued by the publisher. 4. Click the Enable button to allow the macro to run. 5. When you have accepted the macro, return the macro security level to its previous setting.
x | x | x | x | x | x | x | x
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | Q: ‘I cannot find the credit I am interested in as I scroll through a category. Why are they not in order?’
x | x | x | x | x | x | x | x
x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | x x x x x x x x x x x x | As you scroll through a Green Star category, such as IEQ in Education v1, you may find that the credits are not in chronological order. This has to do with the different numbering systems in different tools and we apologise for any inconvenience. If you have difficulty finding a specific credit, please run the find function (CTRL+F) for either the credit number (e.g. ‘IEQ-5’) or by the title of the credit (e.g. ‘Thermal Comfort’). You may also use the sort buttons in Row 5 on each category worksheet. These allow you to sort by Date, Credit number, Title or Type (CIR or Technical Clarification). To remove a filter that you used to sort a column, click on the sort arrow again and select ‘All’. This will restore the original list.
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | Q: 'Why do the clarifications skip a number?'
x | x | x | x | x | x | x | x
x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | x x x x x | A large number of clarifications apply to more than one tool. Therefore, to ensure that there is consistency across the clarifications of all tools, each one has been individually numbered for identification purposes. This numbering is fixed, ensuring that the clarification is easily identified by project teams and the GBCA, and creating a consistent numbering system that can be applied accross all soon to be released tools.
x | x | x | x | x | x | x | x
x x | x x | x x | x x | x x | x x | x x | x x
x x x x x x x x | x x x x x x x x | x x x x x x x x | x x x x x x x x | x x x x x x x x | x x x x x x x x | x x x x x x x x | x x x x x x x x
x | x | x | x | x | x | x | x
x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x
x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x

## Selection
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | Please select the desired rating tool:
x | x | x | x | x | x | x | x
x x | x x | x x | x x | x x | x x | x x | x x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x x | x x | x x | x x | x x | x x | x x | x x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | Technical Clarifications often represent the GBCA answers to technical queries and complement Green Star Technical Manuals (e.g., the Assessment Team will use these Technical Clarifications as public precedent). They do not amend but clarify the Credit Criteria of Compliance Requirements. They are an extension of the Technical Manual; it is the responsibility of the project teams to stay up to date with this section of the website.
x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | x x x x x x x | A Credit Interpretation Request is submitted to the GBCA if a project team wishes to advocate for an alternative yet equivalent method of meeting the Aim of Credit. Each Technical Manual outlines a number of options for meeting the Aim of Credit, but if the project team has developed a alternative design solution or an alternative form of documentation it may wish to submit a CIR. Each CIR is reviewed by 2 members of the Technical Advisory Panel to determine if the solution meets the Aim of Credit. If the CIR is granted, it will be made available to every registered Green Star project and be incorporated into subsequent versions of the Green Star rating tools.
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | The GBCA will issue a correction when an error is identified within a Technical Manual. It will be dated and will only apply to projects registered after the date the correction was issued.
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | © Green Building Council of Australia
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x

## Changelog (hidden)
x | x | x | x | x | x
x | x | x | x | x | x | x | x
x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | Changelog
x | x | x | x | x | x | x | x | Date | Action
x | x | x | x | x | x | x | x | 2008-11-28 | Website release
x | x | x | x | x | x | x | x | 2008-12-17 | - December clarifications released (Select Dec-08 to see the new clarifications)
x | x | x | x | x | x | x | x | 2009-01-20 | - Ene-3 clarification #3 removed from Ov2
x | x | x | x | x | x | x | x | 2009-01-29 | - January clarifications released (Select Jan-09 to see the new clarifications)
x x | x x | x x | x x | x x | x x | x x | x x | 2009-02-13 | - Updated MURT Pilot clarifications. See Ene-4 'Unoccupied Spaces', Wat-4 'Heat Rejection Water', Emi-8 'Legionella'
x | x | x | x | x | x | x | x | 2009-03-17 | - March Clarifications released (Select Mar-09 to see the new clarifications)
x | x | x | x | x | x | x | x | 2009-04-20 | - April Clarifications released (Select Apr-09 to see the new clarifications)
x | x | x | x | x | x | x | x | 2009-05-22 | - May Clarifications released (Select May-09 to see the new clarifications)
x | x | x | x | x | x | x | x | 2009-05-26 | - The Table 'OI IEQ-12 Formaldehyde' has been updated to include particle board
x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | x x x x | 2009-07-29 | - July Clarifications released (Select May-09 to see the new clarifications). - Multi Unit Residential v1 and Healthcare v1 added to the spreadsheet. - Industrial Pilot added to the spreadsheet.
x | x | x | x | x | x | x | x | 2009-05-26 | - Mat-1 No.6 has been updated to include Green Star - Multi Unit Residential, Green Star - Education, Green Star - Healthcare, and Green Star - Industrial Pilot
x | x | x | x | x | x | x | x | 2009-09-28 | Tra-3 No.15 updated to be applicable to all tools
x | x | x | x | x | x | x | x | 2009-10-16 | - October Clarifications released (Select Oct-09 to see the new clarifications).
x | x | x | x | x | x | x | x | 2010-03-23 | - March Clarifications released (Select Mar-10 to see the new clarifications).
x | x | x | x | x | x | x | x | 2010-06-02 | - Changes to the application of CIRs, Technical Clarifications, and Corrections have been announced. See 'Definitions' for more information - Corrections to account for the release of the new 'Steel' and 'PVC' credits released.
x | x | x | x | x | x | x | x | 2010-06-16 | - An update has been made to the ESSENTIAL UPDATES FOR GREEN STAR SUBMISSIONS. See 'Definitions' for more information (NOTE: No changes were made to the Clarifications).
x | x | x | x | x | x | x | x | 2010-11-30 | - December Clarifications released (Select 1-Jan-11 to see the new clarifications).
x | x | x | x | x | x | x | x | 2011-01-12 | Change to Correction 3 for Man-4 Independent Commissioning Agent. This TC only applies to Green Star - Office v2
x | x | x | x | x | x | x | x | 2011-02-22 | Correction to TC 51 for IEQ-11 Volitile Organic Compounds, Level C is excluded. This correction applies to all Green Star tools.
x | x | x | x | x | x | x | x | 2013-09-16 | Spreadsheet renamed 'Green Star Rulings' (previously called TC&CIR Spreadsheet)
x x x x x x x x x x x x x x x | x | x | x | x | x | x | x | 2013-09-16 | The rulings listed below have been removed from Multi Unit Residential v1 as they were not applicable to that rating tool: Mat-9: - TC 2 01/03/09 Emi-3: - DTS-R 01/03/09 Ene-1: - TC 33 01/12/08 Tra-3: - TC 8 01/01/08, CIR 14 01/06/08, TC 23 01/12/08, TC 22 01/12/08, TC 26 01/03/09, CIR 27 01/10/09, CIR 28 01/10/09, CIR 33 01/01/11, Doc A 01/03/09, Doc B 01/03/09 Wat-4: - DTS NV 01/03/09 Emi-8: - DTS NV 01/03/09
x | x | x | x | x | x | x | x | 2013-09-16 | Definitions' tab expanded to address all ruling types, including 'Documentation' rulings.
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | © Green Building Council of Australia
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x

## Definitions (hidden)
x | x | x | x | x | Green Star Rulings | x | x | Green Star Rulings
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x | ESSENTIAL UPDATES FOR GREEN STAR SUBMISSIONS:
x | x | x | x | x | x | x | x
x x x x x x x x | x | x | x | x | x | x | x | Green Star tools continue to evolve after their release date. Updates listed on the ‘Rulings’ database are an essential component of each Green Star tool. The database lists 4 types of rulings: corrections, technical clarifications, credit interpretation request (CIR) rulings and documentation rulings. It is vital to understand their relevance as they may impact the assessment of your project.
x | x | x | x | x | x | x | x
x x | x | x | x | x | x | x | x | TYPE OF RULING | MANDATORY WHEN… | OPTIONAL WHEN… | REQUIREMENTS WHEN USED
x x x x x | x | x | x | x | x | x | x | CORRECTION Overrides previous information in the Green Star tool. | …posted before your project registration date. | …posted after your project registration date. | Comply with the revised information AND include a copy of the correction on your submission cover sheet.
x x x x x x x x x x | x | x | x | x | x | x | x | TECHNICAL CLARIFICATION Extends or clarifies a Green Star requirement. You can request clarification on aspects of the tool by submitting a project specific Technical Clarification through the project manager portal. | …posted before your project registration date. | …posted after your project registration date. | Comply with the revised information AND include a copy of the technical clarification on your submission cover sheet
x x x x x x x x x x x x | x | x | x | x | x | x | x | ‘CIR’ RULING Provide alternative yet equivalent methods of meeting the Aim of Credit that have been approved by the GBCA. You can request approval for a project specific alternative approaching to meeting the aim of a credit by submitting a project specific Credit Interpretation Request through the project manager portal. | Never mandatory. | …approved on the database as a general ruling | Comply with the revised information AND include a copy of the CIR Ruling on your submission cover sheet
x x x x x x x x x x x x | x | x | x | x | x | x | x | DOCUMENTATION These rulings provide information about reductions or changes in documentation requirements for projects. | Never mandatory. | ...issued as a general documentation ruling. | Comply with the revised information AND include a copy of the documentation ruling on your submission cover sheet
x | x | x | x | x | x | x | x
x x x x x x x x | x | x | x | x | x | x | x | All ruling types can be deactivated and classified as ‘withdrawn.’ If this happens after the registration date of your project, you can choose to accept or ignore the ‘withdrawn’ status. If you accept ‘withdrawn’ status for an update that was active at registration, you must comply with any update that supersedes it.
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x

## General (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | General
x | x | x | x | x | x | x | x
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Title | Type | No. | Description | Comments
x | x | x | [5 empty] | 2008-11-01 | Nominated Area | Technical Clarification | 0 | Where stated in this document, nominated area for Green Star - Office refers to NLA.
x | x | x | x | x | x | x | x | 2007-01-01 | GFA | Withdrawn | 1 | (See Clarification General/53 for more information) Gross Floor Area (GFA) is defined as the total floor area of all parts of a building that are permanently covered and can be protected from the elements. Car parking (including under-cover car parking) should not be included in the GFA calculations (as per the Glossary within the Green Star - Office Technical Manuals).
x | x | x | x | x | x | x | x | 2009-03-01 | Interdependent Projects | Technical Clarification | 6 | Originally posted on August 2007 Shared Services and Amenities Both shared and off-site services can contribute to a project's Green Star rating; where projects are unsure of how to document shared services, a Credit Interpretation Request (CIR) must be submitted to invite a GBCA ruling on the manner in which the Certified Assessors are to evaluate compliance. The Green Building Council strongly supports the use of shared / centralised (often those beyond the site boundary of the development being assessed) energy or treatment facilities.
x | x | x | x | x | x | x | x | 2007-08-01 | Interdependent Projects | Technical Clarification | 7 | Examples of Shared Services and Amenities - Car Parking - Peak energy demand reduction facilities - Cyclist facilities - Small car parking spaces - Rainwater/recycled water storage - Recycled water plants
x | x | x | x | x | x | x | x | 2007-01-01 | Interdependent Projects | Technical Clarification | 8 | Shared Energy generation, refrigeration and water treatment services. Energy, Water and Emissions points can be achieved with a shared plant as long as the use by the Green Star development is not jeopardised and not subject to operational uncertainty. The following guidelines apply to these shared services: a. For shared mechanical plants, projects must justify how the plant is apportioned; energy modelling is then conducted for the building as if it were served by a dedicated plant. b. For shared grey- and blackwater treatment facilities, projects must justify how the treatment plant is apportioned. For Wat-1 'Occupant Amenity Potable Water Efficiency', the Potable Water Calculator will estimate the potable water consumption of the building.
x | x | x | x | x | x | x | x | 2007-01-01 | Interdependent Projects | Technical Clarification | 9 | Shared Internal Amenities When the amenity is within the project but other users (for base building projects) or tenants (for fitout projects) are present in the building, the Certified Assessors will seek to validate that the use of such facilities by the project being assessed is not compromised (e.g. that a proportion of facilities is dedicated for exclusive use of the project).
x | x | x | x | x | x | x | x | 2007-08-01 | Interdependent Projects | Technical Clarification | 10 | Shared External Amenities The following applies to amenities that are not within the assessed project: As Green Star assesses inherent attributes of buildings, external amenities can only be rewarded if they are provided for the life of the Building to the same degree of service and certainty as internal facilities, as follows: a. The Building and the amenities are under the same ownership and cannot change ownership separately (i.e. they are on the same title or equivalent); b. The Building and the amenities are under the same management and cannot change management separately (e.g. the same facility management to ensure recycling waste storage is processed as designed); c. There is close, convenient, weather-protected, guaranteed and secure access to the amenities from the Building (and in the case of recycling waste storage, with no step change); d. The amenities are completed by the date of practical completion of the Building; and e. All other elements of the Credit Criteria are met as per the Compliance Requirements and Additional Guidance of the Technical Manual.
x | x | x | x | x | x | x | x | 2007-08-01 | Interdependent Projects | Technical Clarification | 11 | Should any of the Interdependent Projects (see all Interdependent Projects Technical Clarifications) conditions not be met, the external amenities cannot contribute to the Building's Green Star rating or a Credit Interpretation Request (CIR) must be submitted to advocate for alternative yet equivalent compliance. Should the amenities meet the above criteria yet reside in a separate building (from the Building undergoing Green Star assessment), that building can be excluded from the assessment, and only the amenities considered. For example, that building will not be considered for Man-7 'Waste Management', Ene 'Conditional Requirement' or Mat-5 'Concrete' (Office v2 and v3 Tools)/Mat-4 'Concrete' (All Tools). NB: Whenever apportioning is acceptable, the GBCA reserves the right to question the project team's justification for the apportioning, and if it is deemed to compromise the meaning of the outcome or the clarity of the Green Star message, may request reapportioning.
| x | x | [5 empty] | 2010-12-01 | Shell & Core or Integrated Fitout | Technical Clarification | 14 | Originally posted on Jan-08. Green Star – Office Design Certified Rating: The design as documented at tender stage, will be assessed. Delivery after tender documentation is not assessed by this rating. Where the project is designed as an 'integrated fitout', all documentation must address design requirements of the project's prospective tenants. Projects designed for delivery as: 'Shell & Core' or 'Integrated Fitout', must contact the GBCA for more information.
x | x | x | [5 empty] | 2009-04-01 | Shell & Core or Integrated Fitout | Technical Clarification | 15 | Originally posted on Jan-08 Green Star – Office As Built Certified Rating: the project must demonstrate compliance with the Credit Criteria regardless of how the project is delivered (to the extent provided by the base building). Any areas that remain as shell and core (i.e. have not been fitted out) at the time of submission cannot contribute towards the compliance requirements for a credit. For more information, please see the Green Star As Built Guidelines for more information: http://www.gbca.org.au/technical-clarifications-cir-rulings/green-star-as-built-guidelines/1876.htm
x | x | x |  |  |  | x | x | 2009-04-01 | Shell & Core or Integrated Fitout | Technical Clarification | 16 | Originally posted on Jan-08 Any space within a project delivered as a Shell and Core or Integrated Fitout will be assessed on the basis of: - The traditional scope of fitout provided by the base building (e.g. not furniture); - The fully documented design for the relevant Green Star Tool; and - The as-built base building provisions (for a shell and core project) and any fitout provisions installed as part of an integrated fitout (for Green Star – Office As Built). Where any component of the project is delivered as Shell and Core or Integrated Fitout, the General Section of the submission must include an area summary listing each area within the project and indicating whether it is delivered as a standard fitout, integrated fitout or shell and core. In addition, the mode of delivery must be clearly indicated on all documentation to allow for the Certified Assessors to confirm compliance. For more information, please see the Green Star As Built Guidelines for more information: http://www.gbca.org.au/technical-clarifications-cir-rulings/green-star-as-built-guidelines/1876.htm
x | x | [6 empty] | 2008-01-01 | Site Definition | Technical Clarification | 17 | The ‘site’ is defined by the scope of Green Star assessment. If a development consists of several buildings, the site must be defined for each registered building.
x | x | x | x | x | x | x | x | 2008-01-01 | Staged Projects | Technical Clarification | 18 | It is understood that buildings/tenancies are often delivered or refurbished in stages. However, this does not alter the requirements for Green Star submissions, as this would compromise the comparability of Green Star ratings. As such, the entire building/tenancy design is assessed for a Green Star rating, and the documented evidence for each credit must be in full accordance with the relevant Technical Manual. If some aspects of the design have not been completed, projects may not be able to claim affected credits. Similarly, no design documentation will be accepted for an ‘As Built’ assessment and all stages of the project (base building or tenancy - whichever is relevant) must reach practical completion prior to submission.
x | x | [6 empty] | 2006-06-01 | Submission Timing | Technical Clarification | 19 | A project will be about 80% through the design phase before it has enough evidence to submit for Green Star - Office Design. Green Star - Office As Built and Green Star - Office Interiors are assessed after practical completion. For assessment under Green Star - Office Existing Building, the building must be in operation for at least 24 months.
x | x | [6 empty] | 2009-07-01 | Design | Withdrawn | 20 | This Clarification was originally posted on Sep-06. See Clarification No 58 for more information. For assessment under Green Star - Office Design, projects are only responsible for demonstrating compliance for the design as per the Compliance Requirements, even if construction has begun. For example, even if construction of stage one has been completed, a project claiming Man-3 'Commissioning - Building Tuning' must demonstrate commitment to commissioning as stipulated, but does not need to demonstrate commissioning that has taken place for stage one. Similarly, for IEQ-13 'Volatile Organic Compounds', the project must submit specifications and schedules as stipulated, but does not need to submit Manufacturers' Data Sheets. The Certified Assessors will not consider evidence beyond that which is stipulated in the Compliance Requirements.
x | x | x | x | x | x | x | x | 2008-08-01 | Contractual Evidence | Technical Clarification | 28 | Projects can only substitute any documentation, as required by the Technical Manual, with Superintendent Instruction(s), Consultant Advice Notices (CANs) or instructions from the Tenant Representative if they “amend and take precedence over the executed contract, and clearly demonstrate the same level of contractual commitment.” In other words, if no contract, or specification, exists, these letters are not acceptable documentation. The Certified Assessors will not award points to any project which submits these instead of the required contractual documentation. The Certified Assessors will accept Superintendent Instruction(s), Consultant Advice Notices (CANs) or instructions from the Tenant Representative if they meet the requirements of having such documents “amend and take precedence over the executed contract, and clearly demonstrate the same level of contractual commitment” and meet the criteria outlined above.
x | x | x | x | x | x | x | x | 2008-08-01 | Contractual Evidence | Technical Clarification | 28 | Furthermore, for either option above to be seen as equivalent, the project must demonstrate that the instructions were executed. This must be demonstrated via confirmation from the receiving party that the instruction has been received and is being implemented. The relevant extracts from the contractual documentation should also be provided.
x | x | x | x | x | x | x | x | 2007-12-01 | Contractual Evidence | Technical Clarification | 29 | When an extract from the main building contract is required to demonstrate compliance, Superintendent Instruction(s), Consultant’s Advice Notices (CANs) or instructions from the Tenant Representative (wherever appropriate) can be submitted in its place if they amend and take precedence over the executed contract, and clearly demonstrate the same level of contractual commitment, i.e. if either of the following holds true: a. The instructions are endorsed (i.e. counter-signed) by the client; OR b. The client has provided an official and project-specific letter authorising the superintendent, the consultant or the tenant representative to issue contractually binding instructions, and confirming that the client will automatically pay any additional costs associated with these instructions (an upper cost limit may be stipulated).
x | x | x | x | x | x | x | x | 2009-05-01 | ENE-1 ‘ENERGY’, ENE-2 ‘ENERGY IMPROVEMENT’, IEQ-2 ‘AIR CHANGE EFFECTIVENESS’, IEQ-4 ‘DAYLIGHT’, IEQ-5 'DAYLIGHT GLARE CONTROL', IEQ-9 ‘THERMAL COMFORT’, IEQ-12 ‘INTERNAL NOISE LEVELS', TRA-1 'PROVISION OF CAR PARKING', TRA-2 'SMALL PARKING SPACES', TRA-4 'COMMUTING PUBLIC TRANSPORT', AND ECO-1 'ECOLOGICAL VALUE OF SITE' (CONDITIONAL REQUIREMENT), ECO-2 'RE-USE OF LAND'. | Technical Clarification | 42 | Originally posted Jul-08. This clarification has been expanded to include additional credits. As Built projects that have been previously awarded points for credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credits (i.e. same shape floor plan, same type of windows and floor-to-ceiling height) do not need to submit anything besides a letter from the relevant consultant describing the extent of any changes and stating the maximum impact they may have on the building performance if it were remodelled; the number of points achieved in the Design rating will automatically be awarded. Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Please note: This clarification is intended to address just the modeling aspect of credits which require extensive modeling (e.g. Ene-1), or where the attributes of the building are not subject to commissioning (e.g. Tra-4). Where commissioning reports are being requested in these credits, these must still be provided at the time of submission, in addition to the alternative documention listed above.
x | x | x | x | x | x | x | x | 2008-08-01 | For Construction – As Built Drawings | CIR Ruling | 43 | “For Construction” drawings that have been stamped as “As Built” can be deemed equivalent to “As Built” drawings provided that the drawings have been verified “As Built” by the builder subsequent to construction. This must be done via: - A confirmation from the builder or building certifier that the drawings have been verified; OR - Builder’s or Certifier’s signature on the drawings on top of the “As Built” stamp on each drawing.
x | x | x | x | x | x | x | x | 2008-09-01 | Tender documentation | CIR Ruling | 45 | A Request for Information (RFI) is not equivalent to tender documentation.
x | x | [6 empty] | 2008-10-01 | Numbers | Technical Clarification | 46 | The following note in the front page of the spreadsheet: “These numbers are for reference purposes only and are not meant to be used for reference purposes only (e.g. Man-1 Technical Clarification 1)” Has being modified to read: These numbers are for reference purposes only. To ensure that the Certified Assessors have all the information required at the time of assessment, projects must include and highlight the full clarification, as included in the spreadsheet, within the submission.
x | x | [6 empty] | 2008-03-01 | Transfer of changes from new versions of Green Star - Office | Technical Clarification | 47 | Clarifications: As Technical Clarifications provide better guidance or identify common misinterpretations of the Aim of the Credits (which result in credits being denied in assessment), they apply to all projects. Therefore, the clarifications for Green Star - Office v3 apply to all projects undergoing assessment Green Star - Office Design v2 and Green Star - Office As Built v2.
x | x | x | x | x | x | x | x | 2008-10-01 | Contractual documentation | Technical Clarification | 47 | If a credit requires contractual evidence, the Certified Assessors will not award it unless the evidence is clearly of contractual nature, i.e. signed by both parties. Hand written declarations of the contractual nature of documents are not acceptable.
x | x | [6 empty] | 2008-03-01 | Transfer of changes from new versions of Green Star - Office | Technical Clarification | 48 | Changes in criteria: Any change to criteria outlined in the Summary of Changes document apply solely to projects registered for the new versions of the rating tools. Changing any criteria retrospectively jeopardises equitable assessment of all projects. However, achieving higher benchmarks can be claimed for Inn-2 'Exceeding Green Star Benchmarks'. Please note that Innovation points are not guaranteed until approved by the GBCA Board of Directors at the time of the Round 2 assessment.
x | x | x | x | x | x | x | x | 2008-10-01 | Authority Approval | Technical Clarification | 48 | The Certified Assessors will not award any points for an As Built submission, unless all design features that contribute to those points are commissioned (where appropriate) and operating at the time of submission for Green Star Assessment. Where relevant authority approval is required for operating the system as intended by the design (e.g. co-generation systems). Such approval must be submitted at the time of Assessment. In other words, unless the claimed attribute (technology or amenity) is operating, please exclude those attributes from claiming points in the Credit.
x | x | [6 empty] | 2008-06-01 | Transfer of changes from new versions of Green Star - Office | Technical Clarification | 49 | This clarification has been modified to remove reference to the GBCA Board of Directors. The GBCA Directors are in charge of assessing innovation, not the GBCA Board. Originally posted in Mar-08 New credits: Any new credits are available solely to projects registered for the new versions of the rating tools. Changing criteria retrospectively jeopardises equitable assessment of all projects. However, initiatives addressed by new credits can be claimed for Inn-3 'Exceeding Green Star Scope'. Please note that Innovation points are not guaranteed until approved by the GBCA Directors at the time of the Round 2 assessment.
x | x | x | x | x | x | x | x | 2008-12-01 | Contractual Evidence | Technical Clarification | 49 | Where the documentation requirement is a form of contractual evidence, providing a signed letter in its place is not acceptable. The level of 'contractual commitment' provided by a letter (e.g. from a Building Owner to Building Contractor) is not satisfactory. Please see the contractual evidence clarification for more information.
x | x | [6 empty] | 2008-01-01 | Transfer of changes from new versions of Green Star - Office | Technical Clarification | 50 | Switching between versions of Green Star rating tools: Projects registered to receive a Green Star Certified Rating may choose to be assessed using a more recent version of a Green Star Rating Tool as long as it is applied across the entire project (i.e. no partial upgrade is acceptable). The GBCA staff must be notified in writing prior to receiving the project’s submission for assessment. Please note that no project can be assessed under an earlier version (i.e. the version that was superseded by the version in the project’s registration).
x | x | x | x | x | x | x | x | 2008-12-01 | Design & Construct projects (Documentation Guidelines) | Technical Clarification | 50 | If a D&C project (due to the documentation limitations of such projects) cannot supply specifications in meeting specific Criteria of a Credit, the following documents may be submitted as alternatives: - Construction Issue drawings or Tender Issue drawings, provided that they contain the same level of detail as required in a specification and - Site/superintendent/consultant instructions that provide a level of detail similar to that of a specification, and the acceptance of such instructions by the relevant party.
x | x | x | x | x | x | x | x | 2008-12-01 | Definitions | Technical Clarification | 51 | Contractor: Throughout the Technical Manual, “Contractor” refers to the “Head Contractor/Builder”, i.e. the entity responsible for the management of the project’s construction process. Sub-Contractor: Throughout the Technical Manual, “sub-contractor” refers to the trade/discipline specific entity engaged by the Head Contractor to complete a specific part of the project (e.g. the installation of the air-conditioning systems in the case of the mechanical sub-contractor, or the plumbing systems in the case of the hydraulic sub-contractor).
x | x | x | x | x | x | x | x | 2008-08-01 | Design and Construct Projects: Design Submission | Technical Clarification | 52 | It is the responsibility of the project to submit all the information and evidence required for Certified Assessor(s) to properly assess the credit. The Certified Assessor(s) will deny the point(s) for the credit if such information: - Is not available, or - It can be inferred from the documentation that the design is not final and could change prior to construction of the building in a way that will impact the delivery of the building.
x | x | x | x | x | x | x | x | 2008-12-01 | Appendices | Technical Clarification | 52 | The Green Star Pre-Submission Checklist (available at: http://www.gbca.org.au/green-star/certification/submission-assistance/1549.htm) previously stated: - No Appendices are included; all relevant information is within the credit it supports. It now reads: - All relevant information must be included within a credit. Appendices for each credit can be included within a credit provided that they are used for reference purposes only, and highlighted where relevant. Please note: The Certified Assessors are not required to assess any information contained within an appendix. Points will not be awarded for any information or documentation that is not contained within the body of a credit. Where a project wishes to submit information as part of an appendix, this must only be as support, and in addition to, the documentation requested by the Technical Manual (i.e. the relevant page of a specification must be included within the body of the credit, but the project may choose to submit the entire specification as an appendix). However, the Certified Assessors reserve the right to question any discrepancies between any documentation submitted.
x | x | x | x | x | x | x | x | 2008-01-01 | Design vs. As Built | Technical Clarification | 53 | Projects that have achieved a ‘Design’ Certified Rating have a choice of undergoing ‘As Built’ assessment using either the same or the more recent version of the applicable ‘As Built’ tool.
x | x | x | x | x | x | x | x | 2009-02-01 | GFA | Technical Clarification | 53 | (This clarification supersedes Technical Clarification No.1 of this workbook) GFA is the sum of the ‘Fully Enclosed Covered Areas’ and ‘Unenclosed Covered Areas’, as defined by the Australian Institute of Quantity Surveyors (AIQS) Book of Areas. Fully Enclosed Covered Area (FECA): - The sum of all such areas at all building floor levels, including basements (except unexcavated portions), floored roof spaces and attics, garages, penthouses, enclosed porches and attached enclosed covered ways alongside building, equipment rooms, lift shafts, vertical ducts, staircases and any other fully enclosed spaces and useable areas of the building, computed by measuring from the normal inside face of exterior walls but ignoring any projections such as plinths, columns, piers and the like which project from the normal inside face of exterior walls. It shall not include open courts, light wells, connecting or isolated covered ways and net open areas of upper portions of rooms, lobbies, halls, interstitial spaces and the like which extend through the storey being computed.
x | x | x | x | x | x | x | x | 2009-02-01 | GFA | Technical Clarification | 53 | Unenclosed Covered Area (UCA) - The sum of all such areas at all building floor levels, including roofed balconies, open verandahs, porches and porticos, attached open covered ways alongside buildings, undercrofts and useable space under buildings, unenclosed access galleries (including ground floor) and any other trafficable covered areas of the building which are not totally enclosed by full height walls, computed by measuring the area between the enclosing walls or balustrade (i.e. from the inside face of the UCA excluding the wall or balustrade thickness). When the covering element (i.e. roof or upper floor) is supported by columns, is cantilevered or is suspended, or any combination of these, the measurements shall be taken to the edge of the paving or to the edge of the cover, whichever is the lesser. UCA shall not include eaves overhangs, sun shading, awnings and the like where these do not relate to clearly defined trafficable covered areas, nor shall it include connecting or isolated covered ways
x | x | [6 empty] | 2007-12-01 | As-Built documentation for Green Star – Office Design submissions | Withdrawn | 54 | This clarification has been withdrawn. See Technical Clarification No. 65 for more information. (Originally posted on Jan-09) The Credit Interpretation Request (CIR) to provide Green Star – As Built documentation in the place of Green Star – Design documentation for specification-based credits such as ‘Recycled Content of Steel’, ‘Recycled Content of Concrete’ or ‘Sustainable Timber’ is granted. All of the following must be demonstrated: 1. The project began construction prior to registration for Green Star – Design; 2. The Aim of the Credit has clearly been met; 3. All of the documentation for a specific credit is as-built or as-installed in strict accordance with the Green Star – Technical Manual requirements for 'As Built'. Documentation that combines as-built or as-installed documentation with design documentation, is not acceptable.
x | x | x | x | x | x | x | x | 2009-03-01 | Practical Completion | Technical Clarification | 54 | Practical Completion The stage reached when a project has been essentially completed and is fit for its intended purpose, except for minor omissions and defects that do not prevent its use, and with tests required under the contract having been carried out. Practical completion is marked by the issue to the contractor of a certificate of practical completion.” Citation: Real Estate Institute of Victoria, Australian Property Institute & Property Council of Australia (2007), Glossary of property terms, Canberra: REIV, API & PCA.
x | x | [6 empty] | 2007-12-01 | Digital Evidence | Technical Clarification | 55 | The GBCA will accept electronic documentation such as e-mails, digitally signed/stamped (e.g. ‘As Built’ stamp) drawings and letters, and documentation from an internal document management system (e.g. Aconex), as part of a submission for most documentation, provided that the Certified Assessor(s) can attest that the documentation submitted is complete, meets the criteria outlined in the Technical Manual, and its integrity cannot be questioned.
x | x | x | x | x | x | x | x | 2009-03-01 | Developer/Owner & Contractor documentation | Technical Clarification | 55 | Where the Developer/Owner and Contractor of the project are the same entity, it is sufficient to provide specifications wherever a contract between these two parties is required.
x | x | [7 empty] | GFA and NLA | Technical Clarification | 56 | Please note that in regards to GFA and NLA, whenever the Credit Criteria refers to NLA ('Air Change Effectiveness', 'Daylight' or 'Recycling Waste Storage'), only Class 5 Commercial Office areas must be included in the assessment; however, when the Credit Criteria refers to the entire project ('Waste Management', 'Formaldehyde Minimisation' or 'Recycled Content of Concrete'), the entire project, including the internal car parks and non-office areas, must be assessed.
x | x | [6 empty] | 2007-12-01 | Digital Evidence | Technical Clarification | 57 | All documentation must be in the form of PDF printed versions of the documents, including e-mails. Because of the different types of file formats, and the difficulty in obtaining the software required in viewing them all, the GBCA will not accept any other type of file formatting. Please note that some documentation, such as contractual documentation, cannot be submitted in the original electronic formatting. These must be physically signed by the relevant parties, scanned, and turned into PDF for submission. The GBCA reserves the right to further identify unacceptable forms of digital evidence, and to expand the list of acceptable examples below. Please email greenstar@gbcaus.org if further clarification or confirmation is required.
x | x | x | x | x | x | x | x | 2009-03-01 | Relevant Authority Approval for federal government land (Wat-1 ‘Occupant Amenity Potable Water Efficiency’ (Emi-6 ‘Reduced Floor to Sewer’) and Eco-1 ‘Ecological Value of Site’) | CIR Ruling | 56 | The Credit Interpretation Request to have the Defence Estate Policy and Environment Branch (DEPE) be deemed equivalent to the relevant local and state authority is granted conditionally, for federal government land where local council planning requirements do not apply, and, where the project is of Defence nature, on the projects ability to demonstrate that DEPE will certify, and act as the authority approval for: - The installation of a water treatment plant and sewerage treatment plant (Wat-1 ‘Occupant Amenity Potable Water Efficiency’ (Emi-6 ‘Reduced Floor to Sewer’ credits), and - Confirming that the development was not prime agricultural land or within 100m of a natural wetland (Eco-1 ‘Ecological Value of Site’ credits). The project must submit a letter from DEPE that contains this information as well as the applicable relevant standards to which the project will be submitted to.
x | x | [6 empty] | 2008-03-01 | Differences between Green Star - Office Design v2 and Green Star - Office As built v2 | Technical Clarification | 57 | The Green Star - Office Design and Green Star - Office As Built Rating Tools are intended to directly relate to one another. However, there are some instances (e.g. Eco-5 'Topsoil & Fill Removal from Site) where the Technical Manual conflicts regarding how points are awarded. For projects that have been certified under Green Star - Office Design v2, the same criteria applies for Green Star - Office As Built v2. For projects applying only for Green Star - Office As Built, the criteria apply exactly as per the Technical Manual. In order to resolve any conflict, these tools have been combined into one cohesive Technical Manual: Green Star - Office v3.
| x | [6 empty] | 2009-03-01 | Design/As Built | Technical Clarification | 57 | A Green Star - Design certified project seeking a Green Star - As Built rating cannot use the Credit Criteria of the Design tool for credits not claimed during the Design submission. They must use the criteria for Green Star - As Built.
x | x | [6 empty] | 2007-12-01 | Digital Evidence | Technical Clarification | 58 | Examples of Digital Evidence Example: A printed copy of the full e-mail instruction, all headers included. Where e-mails are being submitted as superintendent instructions, the e-mails printed must come from all involved parties, signaling that they have understood and are implementing the instructions. Single e-mails setting out requirements or making requests cannot be used to comply with the submission requirements as per the CIR posted on the GBCA website. Example: Digitally signed/stamped drawings printed straight from the CAD software which is being used in the project. Stamps applied to drawings via a PDF editing software will not be accepted.
x | x | x | x | x | x | x | x | 2009-07-01 | Design | Technical Clarification | 58 | The following is being clarified: For assessment under Green Star - Office Design, projects are only responsible for demonstrating compliance for the design as per the Compliance Requirements, even if construction has begun. For example, even if construction of stage one has been completed, a project claiming Man-3 'Commissioning - Building Tuning' must demonstrate commitment to commissioning as stipulated, but does not need to demonstrate commissioning that has taken place for stage one. Similarly, for IEQ-13 'Volatile Organic Compounds', the project must submit specifications and schedules as stipulated, but does not need to submit Manufacturers' Data Sheets. The Certified Assessors will not consider evidence beyond that which is stipulated in the Compliance Requirements. This clarification refers to the initial submission made by the project team. At Round 1, for purposes of Green Star - Design, the assessment is carried out as though no work had begun on site. Therefore, only tender documentation is required. However, if a project is under construction at the time of Round 1 assessment, the Certified Assessors will take this into account when requesting additional information for Round 2. For example, if the credit 'Concrete' is claimed, at Round 1, the certified assessors will assess the documentation provided based on the Compliance Requirements. If part of the documentation, such as the extracts from the specification(s), are found not to meet the compliance requirements, the assessors can ask for additional documentation demonstrating that the concrete used in the building met the criteria. This can be provided in the form of extracts of the contractual documentation, delivery dockets, or confirmation from the concrete supplier. Note: 1) Any design changes made as a result of Round 1 must be executed in the main contract. Please see Technical Clarification General/28 for more information. 2) Projects can submit As Built documentation at the time of Green Star - Design submission. Please see Technical Clarification General/18 for more information.
x | x | x | x | x | x | x | x | 2009-07-01 | Definition of Worksetting | Technical Clarification | 59 | The following rules apply to defining worksettings for purposes of Green Star: - A workstation is 1 worksetting; - Any two visitor chairs at the workstation is NOT considered a worksetting; - Meeting tables are considered worksettings. In this case, every two chairs is a worksetting. For example, a 6 person meeting table is considered to have 3 worksettings; - 2 chairs at an informal table (ie. breakout space) are 1 worksetting (unless in can be clearly shown that no work will commonly occur in this space) - Every 2nd chair in a training room, auditorium, lectural hall, or similar is considered a worksetting. As a simple example, 4 chairs in a row are 2 worksettings, just as 5 would be considered 2 worksettings. Seating in a cafe area or guest seating in reception or lobby areas are not considered worksettings.
x | x | x | x | x | x | x | x | 2009-07-01 | Commissioning for Green Star - As Built projects | Technical Clarification | 60 | If the commissioning credits are not claimed, a minimum standard of commissioning is still required. The Green Building Council will not accept any extracts from the commissioning report from an as-built submission that do not state: - method of commissioning with clearly documented acceptance criterion - commissioning sheets - modifications made to the system where the acceptance criterion has not been met. All documentation must be project specific and dated.
[5 empty] | x |  |  | 2009-07-01 | Green Star - Healthcare | Technical Clarification | 61 | Table App-A.2 on page 462 (Green Star – Healthcare v1 State Based Weighting Factors) of the Green Star –Healthcare v1 technical manual contains an error. The total number of points in the tool is 159 (not 157). There are a total of 29 points in the Energy category (not 28), and a total of 30 points in the materials category (not 29).
x | x | [6 empty] | 2009-08-01 | Green Star- Office Design vs. Green Star - Office As Built | Withdrawn | 62 | See clarification No. 58 for more information. Originally posted in Mar-08 Does the submission for Green Star - Office Design need to demonstrate evidence of implementation if construction has commenced? For assessment under Green Star - Office Design, projects are only responsible for demonstrating compliance for the design as per the Compliance Requirements, even if construction has begun. For example, even if construction of stage one has been completed, a project claiming Man-3 'Commissioning - Building Tuning' must demonstrate commitment to commissioning as stipulated, but does not need to demonstrate commissioning that has taken place for stage one. Similarly, for IEQ-13 'Volatile Organic Compounds' the project must submit specifications and schedules, as stipulated, but does not need to submit Manufacturers' Data Sheets. The Certified Assessors will not consider evidence beyond that which is stipulated in the Compliance Requirements.
x | x | x | x | x | x | x | x | 2009-05-01 | Technical Clarifications | Correction | 62 | Technical Clarifications (TC) Please see the 'Definitions' tab for more information.
x | x | x | x | x | x | x | x | 2009-05-01 | Credit Interpretation Requests | Correction | 63 | Credit Interpretation Requests (CIR) Please see the 'Definitions' tab for more information.
x | x | [6 empty] | 2008-01-01 | Initial Condition | Technical Clarification | 64 | For the purposes of credits that require comparison between the initial and resulting conditions of the site, e.g. Mat-2 ‘Reuse of Façade’, Mat-3 ‘Reuse of Structure’ or credits in the Land Use and Ecology Category, the initial condition is defined as the condition at the time of site purchase, and can be documented through evidence (e.g. aerial photographs or site plans) generated at or before the time of purchase.
x | x | x | x | x | x | x | x | 2009-05-01 | Corrections | Correction | 64 | Corrections Please see the 'Definitions' tab for more information.
x | x | x | x | x | x | x | x | 2011-01-01 | As-Built documentation for Green Star – Office Design submissions | Technical Clarification | 65 | While 'Tender' stage drawing sets are usually submitted for a Green Star - Design rating, 'As Built' stage drawing sets are also acceptable.
x | x | x | x | x | x | x | x | 2007-08-01 | Assumptions | Technical Clarification | 66 | It is acceptable to use assumptions (e.g. in regards to thermal and visual properties of an existing façade) in demonstrating compliance with the Credit Criteria, but only when actual values/properties are not known and the submission must clearly justify that at all times, the assumptions have been conservative. Should any project seek confirmation whether its assumptions are sufficiently conservative, CIRs justifying the assumptions must be submitted.
|  | x | [5 empty] | 2011-01-01 | General | Withdrawn | 66 | This ruling has been withdrawn as of 01-Nov-13. Please refer to ruling number 75. Credit criteria may be concerned with certain parts of the building, rather than the whole building. Where this is the case, a 'nominated area' is specified. Where no nominated area is specified, the credit criteria deals with the whole building. Nominated area has been incorrectly described in the Green Star - Office v3 technical manual, for some credits. For the following credits, the nominated area is 'Class 5 Office Net Lettable area', NOT 'Net Lettable Area': - IEQ-2 ‘Air Change Effectiveness’ - IEQ-10 ‘Individual Comfort Control’ - IEQ-12 ‘Internal Noise Levels’ - IEQ-16 ‘Tenant Exhaust Riser’ - Ene-3 ‘Lighting Power Density’ - Ene-4 ‘Lighting Zoning’ - Mat-4 ‘Shell and Core or Integrated Fitout’ Definitions: Net Lettable Area (NLA): This includes any area, regardless of its use or function, included in the NLA measurement defined in 'Method of Measurement', written by the Property Council of Australia. Class 5 Net Lettable Area: This includes only Class 5 spaces found within the Net Lettable Area. Class 5 spaces: Spaces that are defined as Class 5, by the 'Building Code of Australia'.
x | x | x | x | x | x | x | x | 2007-08-01 | Assumptions | Technical Clarification | 67 | Should design change between the Round 1 and Round 2 submissions, the Certified Assessor(s) will seek to verify consistency for all contingent credits in order for those credits to contribute to the project's final rating, even if they were awarded in the Round 1. This may require that certain evidence be resubmitted for previously awarded credits to demonstrate such consistency. For example, if a peak energy demand reduction system has been introduced, it must be accommodated in the commissioning credits for all relevant services, such as Man-2 'Commissioning - Clauses', Man-3 'Commissioning - Building Tuning', Man-4 'Commissioning - Commissioning Agent', Man-5 'Building Users' Guide' and IEQ-12 'Internal Noise Levels' (v3 Tools)/IEQ-7 'Internal Noise Levels' - and wherever else it might affect compliance.
x | x | x | x | x | x | x | x | 2011-01-01 | Relevant local consent Authority | Technical Clarification | 67 | If part or all of a project site is not governed by by a local council, a CIR must be submitted. The CIR ruling should determine the most appropriate body to act as local consent authority for the project's documentation.
x | x | x | x | x | x | x | x | 2011-01-01 | Drawings | Withdrawn | 68 | This ruling has been withdrawn as of 01-Jul-12. Please refer to ruling number 81. Drawings marked as ‘record drawings’ can be submitted in lieu of ‘as built’ drawings as long as they are accompanied by a drawing transmittal that demonstrates that the record drawings have been issued as a final set.
x | x | [6 empty] | 2008-01-01 | Round 2 Submission | Technical Clarification | 69 | Where the Certified Assessor(s) request that a piece of evidence be resubmitted in order for the credit to be awarded, it is the responsibility of the project team to resubmit the entire credit, and the related credits, if the revised evidence changes the basis on which the rest of the evidence was accepted in Round 1. The Certified Assessor(s) will seek to confirm that all evidence clearly and consistently confirms compliance, and reserve the right to withdraw credits awarded in Round 1 if a subsequently demonstrated change would necessitate re-assessment.
| x | x | x | x | x | x | x | 2011-01-01 | General | Technical Clarification | 69 | Where projects register for an As-built rating after a Design rating has been achieved, the registration date of the Design rating will be used to determine applicability of Techncial Clarifications, Credit Interpretation Requests and Corrections.
x | x | x | x | x | x | x | x | 2007-01-01 | Eligibility | Technical Clarification | 70 | If ever in doubt whether a project meets the Eligibility Criteria, projects must get a confirmation or refutation from the GBCA. Please refer to the GBCA website on Eligibility (http://www.gbca.org.au/green-star/certification/), complete a Green Star Project Eligibility Template form and send it to greenstar@gbca.org.au.
x | x | [6 empty] | 2006-06-01 | Round 2 Submission | Technical Clarification | 71 | Projects are welcome to both claim additional credits and even change design between Round 1 and Round 2. However, please note the following: a) all new information only gets one review (i.e. new information does not qualify a project for Round 3), and; b) explicitly inform the Certified Assessor(s) (e.g. in the general section via a cover letter) where new information lies, as otherwise they will only review the items in question.
x | x | [6 empty] | 2007-01-01 | Eligibility | Technical Clarification | 72 | To protect the Green Star brand for the sake of all certified and registered projects, the GBCA has and will refuse assessment to any project that does not meet the Eligibility Criteria. (see: http://www.gbca.org.au/gbca.asp?sectionid=96&docid=960) The GBCA has requested resubmissions when a portion of a building/fitout was submitted for assessment.
x | x | [6 empty] | 2006-06-01 | Round 2 Submission | Withdrawn | 73 | There has been a change in the process for addressing round 2 submissions, please seek advice from your Case Manager. The project need ONLY resubmit credits/items that were questioned by the Certified Assessor(s). Hence, the Round 2 submission should be very thin, and explicitly address the comments received after the Round 1. Where the Certified Assessor(s) request that a piece of evidence be resubmitted in order for the credit to be awarded, it is the responsibility of the project team to resubmit the entire credit, and the related credits, if the revised evidence changes the basis on which the rest of the evidence was accepted in Round 1. The Certified Assessor(s) will seek to confirm that all evidence clearly and consistently confirms compliance, and reserve the right to withdraw credits awarded in Round 1 if a subsequently demonstrated change would necessitate re-assessment.
x | x | x | x | x | x | x | x | 2007-08-01 | Shared Services | Technical Clarification | 74 | For information on Shared Services select Interdependent Projects in the Topic Column (No. 6, 7, 8).
|  | x | x | x | x | x | x | 2009-03-01 | Documentation Guidelines | Documentation | A | This document applies to all projects regardless of when registration occurred. All projects have the option of using, for each credit, the revised documentation according to this guideline or the Technical Manual. If any documentation guideline is used, it must be used in its entirety.
|  | x | x | x | x | x | x | 2009-03-01 | Documentation Guidelines | Documentation | B | Where a project is submitting the modified documentation for assessment, they must state on their cover sheet the relevant guideline as taken from this spreadsheet.
|  | x | x | x | x | x | x | 2009-03-01 | Documentation Guidelines | Documentation | C | The Credits listed above require that Evidence of site purchase and Site documentation be provided at the time of submission. This often results in a large amount of repeated information. To avoid this repetition, projects may provide the following in the General section of the submission, and simply refer to these evidence in the related credits. Projects choosing to use this approach must submit the following documentation in the General Section of the submission. * Evidence of site purchase showing the state of the site at the time of purchase. This evidence must show whether the site was a greenfield or brownfield site, and whether it contained any buildings at the time of purchase. * Site documentation such as scaled site plans OR aerial photographs generated at or prior to site purchase, showing: - The proposed built area for the new development indicated and quantified; - Where the site contains any existing buildings, showing the footprint area of the existing buildings and the area of the new buildings; and - Identifying the land types present on site in accordance with Eco-4 'Change in Ecology Calculator'; - Showing, and identifying the areas in a radius no less than 100metres around the site.
x |  | x | x | x | x | x | x | 2011-01-01 | Redevelopment Documentation Guidelines | Withdrawn | D | This clarification has been withdrawn. See General section for Land Use & Ecology for further information. (Originally posted Oct-09) Some redevelopment projects require identical records of site purchase and site conditions to be provided for several credits. A Green Star submission for redevelopment, is only required to provide one copy of these records. When a submission provides only one copy of site records, the following conditions apply: - The records must be placed in the 'General' section of the submission - Clear references must be provided, wherever one of these records is used as part of documentation for a credit - All of the following records must be provided in the 'General' section: - Evidence of site redevelopment showing the state of the site at least two years prior to site redevelopment. This evidence must show whether the site was a greenfield or brownfield site, and whether it contained any buildings. - Site documentation such as scaled site plans OR aerial photographs generated prior to site redevelopment, showing all of the following: - Location, footprint and square metre area of the proposed new development; - Location, footprint and square metre area of any existing buildings on the site; - Identification of the land types present on site, in accordance with the 'Change in Ecology Calculator' in the Land Use and Ecology category; - Identification of the land types of all areas within 100 metres of the site.
x | x | [6 empty] | 2008-01-01 | Alternatives to specifications | CIR Ruling | 75 | The Credit Interpretation Request to deem the inclusion of the details of the design criteria within the base building scope of works contract equivalent to the inclusion of the same information within the structural specification is granted. The Certified Assessor(s) will, however, look for a similar level of certainty to that expected from the structural specifications.
x | x | x | x | x | x | x | x | 2008-01-01 | Alternatives to specifications | CIR Ruling | 76 | The Credit Interpretation Request to deem construction drawings equivalent to a specification is granted conditionally on the project's ability to clearly demonstrate the following: - The construction drawings contain all the information required in the Technical Manual to define the design and scope of work; - A short report from a suitably qualified Engineer is provided and describes how the Credit Criteria is met; and - All other documentation for this credit is provided in accordance with the Technical Manual. The Certified Assessor(s) will look for a similar level of certainty to that expected from the specifications.
x | x | x | x | x | x | x | x | 2006-09-01 | Documentation Submission | Technical Clarification | 77 | In order to be assessed, projects must limit their submissions to the specific documentation stipulated in the Compliance Requirements in the Technical Manual. The GBCA cannot allocate resources for reviewing superfluous documentation. Therefore, if complete project specifications are submitted for assessment, the entire submission will be returned to sender.
x | x | [6 empty] | 2006-09-01 | Documentation Submission | Technical Clarification | 78 | The Assessor(s) reserve the right not to review any documentation that is not in Word or PDF format. If change in design occurs between the Round 1 and Round 2 assessment, the client must submit a letter of confirmation that the variations (e.g., within engineers' instructions) are accepted and acted upon.
x | x | [6 empty] | 2007-12-01 | Documentation Submission | Technical Clarification | 79 | Please ensure the Pre-Submission Checklists are completed for respective Rounds of Assessment, and notify the GBCA of your submission via the Submission Notification Form.
x | x | x | x | x | x | x | x | 2012-08-01 | Design & Construct projects (Documentation Guidelines) | Technical Clarification | 80 | The project team may demonstrate changes to the original specifications by providing the following: - A letter from the sub-contractor to the issuer of the original specification requesting approval for the design change. The letter must clearly reference the design requirement detailed in the original specification; - A letter of acceptance from the issuer of the original specification clearly stating the approved change amends and takes precedence over the design requirement as detailed in the original specification; - Approved ‘For Construction’ drawings or schedules that reflect the final approved design; and, - A copy of the original specification.
x | x | x | x | x | x | x | x | 2012-08-01 | Documentation - Drawings | Technical Clarification | 81 | The following can be considered equivalent to 'As-Built' issue drawings, provided the project team includes a signed statement from the architect including the full drawing transmittal that demonstrates the submitted drawings were issued as a final set: 'Final Construction' 'As Executed' 'As Installed' 'For Record' The statement from the architect and drawing transmittal should be included with the general section of the project submission.
x | x | x | x | x | x | x | x | 2012-08-01 | Authority Approval | Technical Clarification | 82 | The ‘relevant authority’ is the appropriate authority who is responsible for providing a particular permission or which oversee a particular regulation. This may be the local council, state government, federal government, Environmental Protection Authority, or other authority. The ‘relevant authority’ varies for different states, locations, and type of project. This is why the Technical Manual does not stipulate a specific body. The project must ensure that the appropriate authority has been selected, and they have provided the information required in the Technical Manual (and any Technical Clarifications or CIR’s).
[6 empty] | x |  | 2012-08-01 | GLA | Technical Clarification | 83 | The Green Star - Industrial v1 Technical Manual specifies that the Gross Lettable Area (GLA) will be in accordance with the Property Council of Australia ‘Method of Measurement 1997’ guidelines. According to these guidelines, in single tenanted building this includes: - Amenities - Stairs/Fire stairs - Telecommunication cupboards (comms cupboards, data rooms) - Cupboards, fire hose reel cupboards - Escalators - Plant/motor rooms - Lifts However, there are several credits for which these areas should not be included in the GLA, as their inclusion would provide minimal benefit to the environment and/or building users. The areas listed above should be excluded from the GLA for the following credits: - IEQ-1 Ventilation Rates - IEQ-2 Air Exchange Effectiveness - IEQ-3 CO2 Monitoring & Control and VOC Monitoring - IEQ-4 Daylight IEQ-5 Thermal Comfort - IEQ-13 Electric Lighting Levels - IEQ-17 Air Distribution System
x | x | x | x | x | x | x | x | 2012-08-01 | Documentation - As Built and Design | Technical Clarification | 84 | Within design ratings it is acceptable to provide tender documentation for one credit and as-built documentation for another credit, as long as the information provided is not in contradiction. The certified assessors will look for consistency throughout the documentation provided, and may deny any credit if information is inconsistent with that submitted for another credit. A combination of As Built and Design documentation is allowable within credits. If as built documentation is used, the following is required: Include a comment on the credit cover sheet nominating any As Built documentation used and explaining why it was necessary to submit in that form; Ensure any as-built documentation submitted is in full accordance with the as-built requirements of the Technical Manual.
|  | x | [5 empty] | 2013-11-01 | General | Technical Clarification | 85 | The Green Star rating tools apply to the entire Green Star project boundary unless otherwise specified within individual credits. In instances where a credit is applicable to a ‘nominated area’, this is defined by the specific credit. The ‘nominated area’ for the following credits is being corrected to apply to BCA Class 5 Net Lettable Area only: - IEQ-1 ‘Ventilation Rates’ - IEQ-2 ‘Air Change Effectiveness’ - IEQ-3 ‘Carbon Dioxide Monitoring & Control’ - IEQ-4 ‘Daylight’ - IEQ-5 ‘Daylight Glare Control’ - IEQ-10 ‘Individual Thermal Comfort Control’ - IEQ-12 ‘Internal Noise Levels’ - IEQ-15 ‘Mould Prevention’ - IEQ-16 ‘Tenant Exhaust Riser’ - Ene-3 ‘Lighting Power Density’ - Ene-4 ‘Lighting Zoning’ - Tra-3 ‘Cyclist Facilities’ - Mat-4 ‘Shell and Core or Integrated Fitout’ Definitions: Class 5 Net Lettable Area: This includes only Class 5 spaces defined as the Net Lettable Area. Please refer to the Property Council of Australia’s ‘Method of Measurement’(2004)
X | X | X | X | X | X | X | X | 2013-11-01 | General | Technical Clarification | 86 | Where specifications are required to be submitted as part of credit submissions, either of the following approaches to presenting these specifications is acceptable: 1. Green Star compliant specification clauses are integrated within each individual service’s specifications; OR 2. A Sustainability specification (also called an ESD specification) is developed containing all Green Star and ESD related specification clauses. In order for this to be deemed equivalent, the service’s/ sub-contractor’s specifications must make reference to the ESD Specification and it must be included as an annex or appendix to that specification. Where this approach is adopted, the following must be provided wherever specification extracts are required: - The relevant section of the ESD or Sustainability Specification; and - The section within the relevant services specification referring to the ESD or Sustainability Specification (this reference must quote the actual name of the project's ESD or Sustainability Specification).
[7 empty] | x | 2013-11-01 | General | Technical Clarification | 87 | The following clarifications are provided in instances where a multi-unit residential development also includes other uses (for example retail or commercial). The following credits are only applicable to residential spaces (i.e. only apply to BCA Class 1a or Class 2 areas). - IEQ-4 ‘Daylight’ - IEQ-5 ‘Thermal Comfort’ - IEQ-7 ‘Internal Noise Levels’ - IEQ-13 ‘Electric Lighting Levels’ - IEQ-20 ‘Private Outdoor Space’ - IEQ-21 ‘Dwelling Ventilation’ - IEQ-22 ‘Natural Ventilation’ - Ene-Conditional - Ene-1 ‘Greenhouse Gas Emissions’ - Ene-7 ‘Unoccupied Spaces’ - Ene-11 ‘Energy Efficient Appliances’ - Ene-12 ‘Peak Electricity Demand Reduction’ - Tra-1 ‘Provision of Car Parking’ - Tra-2 ‘Fuel Efficient Transport’ - Tra-3 ‘Cyclist Facilities’ - Wat-1 ‘Occupant Amenity Water’ - Wat-7 ‘Water Efficient Appliances’ - Mat-1 ‘Recycling Waste Storage’ - Mat-15 ‘Universal Design’ - Emi-6 ‘Discharge to Sewer’ For all credits not mentioned within this ruling, compliance must be demonstrated for the entire Green Star project site or building in accordance with the detail of each credit.
X | X | X | X | X | X | X | X | 2013-11-01 | General - Commissioning | Technical Clarification | 88 | Where documentation calls for *Extract(s) from commissioning report, in place of the requirements as listed in the Technical Manual these extracts must include: - a contents page or chapter headings which confirm that all relevant systems have been included in the commissioning process. - A sign off page demonstrating that the commissioning report and commissioning process has been signed off by all relevant parties including: services engineers, sub-contractors, and the ICA (if an ICA has been engaged) or commissioning manager (if no ICA has been engaged). No further information needs to be provided where commissioning reports are called for.
X | X | X | X | X | X | X | X | 2013-11-01 | General - Commissioning | CIR Ruling | 89 | Documentation (As-Built) Where technical manual calls for *Extract(s) From Commissioning Report the project team may instead submit a Certificate of Readiness for all relevant systems. This document must confirm that the relevant systems have been commissioned in line with documented design, commissioning methods used are in line with a relevant commissioning code. This document must be countersigned by the ICA (if engaged) or commissioning manager (if no ICA engaged on project), relevant sub-contractors, relevant services design engineers and the client (or client representative). For a reference certificate of readiness please see CIBSE Guide M Appendix MA4.

## Man (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Management
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | X | X | X | X |  | Man-0 | Man-0 | Man-0 | Man-0 | General
x | x | x | x | X | X | X | X |  | Man-1 | Man-1 | Man-1 | Man-1 | Green Star Accredited Professional
x x x x | x | x | x | x | x | x | x | 2011-10-01 | Man-1 | Man-1 | Man-1 | Man-1 | Please note there is a revised version of this credit which was released in August 2011. If your project was registered after 01/10/2011, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/man-1-green-star-accredited-professional-credit/3897.htm
x | x | x | x | x | x | x | x | 2007-12-01 | Man-1 | Man-1 | Man-1 | Man-1 | Green Star Accredited Professional | Technical Clarification | 1 | If the schematic design phase of a project commenced prior to the development of the Green Star rating system and the accompanying training course, the project will not be eligible for this point as an equivalent level of advice would not be available.
x | x | [6 empty] | 2008-01-01 | Man-1 | Man-1 |  |  | Green Star Accredited Professional | Technical Clarification | 2 | It is understood that in some circumstances, the role of the Green Star Accredited Professional is fulfilled by different individuals throughout the project. This is acceptable as long as each Green Star Accredited Professional individually meets the requirements of this credit and this role has been fulfilled continually from the beginning of the schematic design.
x | x | x | x | x | x |  | x | 2008-06-01 | Man-1 | Ma | Man-1 | Man-1 | Green Star Accredited Professional | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem a list of roles and responsibilities and a letter from the client confirming the Green Star Accredited Professional’s involvement in the project instead of a letter of appointment is granted. Please note that this does not guarantee the points for this credit. The Green Star Accredited Professional must still meet all Compliance Requirements outlined in the Technical Manual, the team must show that the participant was a Green Star Accredited Professional, and that the person was involved in the project from the beginning.
x | x | x | x | X | X | X | X |  | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning
x | x | [6 empty] | 2007-12-01 | Man-2 | Man-2 |  |  | Commissioning - Clauses / Tenancy Fitout Commissioning | Correction | 1 | As stated in the Credit Criteria section of the credit, this credit addresses the commissioning of all systems, not just of the mechanical systems. ASHRAE addresses mechanical systems only; therefore, if used, it must be supplemented by CIBSE for all other systems.
x | x | [6 empty] | 2008-09-01 | Man-2 | Man-2 |  |  | Commissioning - Clauses / Tenancy Fitout Commissioning | Technical Clarification | 2 | Instead of: “The following information must be included (as a minimum) in the commissioning report provided to the tenant and/or base building owner.” It should read: “The following information must be included (as a minimum) in the submission and provided to the tenant and/or base building owner.”
x | x | x | x | x | x |  | x | 2008-12-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Technical Clarification | 3 | Projects undertaking a Green Star - As Built rating: The Technical Manual notes that to be awarded the second point, "A complete set of as-built drawings for all mechanical, electrical and hydraulic systems and a comprehensive Operations and Maintenance (O&M) manual" must be provided as part of the building owner/manager documentation requirements. This requirement is being revised as follows: - A Copy of the Title/Index/Contents Page of the Operations & Maintenance manual. - A drawing register listing the drawing name, number and issue of all as built drawings; - A copy of the transmittal showing that these documents were sent to the owner. The transmittal must be detailed, with the drawing number/name/revision number clearly listed for each drawing/document that was issued; and - A letter from the owner/manager of the building stating that all the documents have been received. The letter MUST explicitly say exactly what documents were received by the owner/manager and mention that the owner is satisfied that the building was delivered as per the documented design. All other documentation must be submitted as per the technical manual.
x | x | x | x | x | x |  | x | 2008-12-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Technical Clarification | 4 | Where the Developer/Owner and Contractor of the project are the same entity, it is sufficient to provide specifications wherever a contract between these two parties is required.
x | [7 empty] | 2013-11-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Correction | 5 | The paragraph below replaces the second last paragraph on page 4 of Man-2 beginning ‘Reference should be made to the importance...’ Whilst it is not required by the referenced standards, project teams are strongly encouraged to consider the implications of commissioning on indoor air quality, for example through establishing an indoor air quality commissioning plan at the design stage with specific provisions for ensuring that this plan is met during and after commissioning. It should be noted that the above: • should be considered as additional advice only. It is additional information to guide project teams in preparing their submissions but does not from part of the credit’s Compliance Requirements. • does not relate to what the required training should include/address. only that which is in the table is relevant to training.
|  | x | x | x |  |  |  | 2009-03-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Project Timeline. In order to show that the building owner is aware of the time required for effective commissioning, the Confirmation from the building owner must clearly state the time related requirements of the pre-commissioning, commissioning, and quality monitoring required by the credit criteria. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x | 2011-01-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Technical Clarification | 5 | The Technical Manual describes what must be provided in the design intent report in order to achieve a point. It lists three items that must be included as a minimum: - Energy and Environmental Strategies and Features - Monitoring and Targeting Details; and - Building Services Description. These three items must be included in the Design Intent Report as described in the Technical Manual. The complete Design Intent Report must be provided in full in a Green Star – Design submission and in a Green Star – As Built submission. The submission of partial or draft reports will result in the additional point to not be awarded in this credit.”
x | x | x | x | x | x | x | x | 2012-08-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Technical Clarification | 7 | The Credit Criteria for Man-2 (all tools) states that commissioning can be performed in accordance with ASHRAE Guideline 1-1996 (for mechanical services only) and CIBSE Commissioning Codes for other services. In addition to the documents outlined in the credit, the following two application manuals are now recognised as an appropriate standard for commissioning within this credit: - AIRAH application manual DA 27 Building Commissioning – 2011. This guide provides a comprehensive and Australian guide to building commissioning, similar to CIBSE Commissioning Codes. - AIRAH application manual DA 28 Building Management and Control Systems (BMCS) – 2011. This guide provides a comprehensive and Australian guide to controls and Building Management and control systems. These two guides must be used in unison. Where the credit states ‘CIBSE Commissioning Codes’, the credit should now be read as stating ‘CIBSE Commissioning Codes or both AIRAH DA27 and DA28’.
x | x | x | x | x | x | x | x | 2012-08-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: - Project Timeline. In order to show that the building owner is aware of the time required for effective commissioning, the Confirmation from the building owner must clearly state the time related requirements of the pre-commissioning, commissioning, and quality monitoring required by the credit criteria. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x | 2012-08-01 | Man-2 | Man-2 | Man-2 | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: - Project Timeline. In order to show that the building owner is aware of the time required for effective commissioning, the Confirmation from the building owner must clearly state the time related requirements of the pre-commissioning, commissioning, and quality monitoring required by the credit criteria. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | X | X | X | X |  | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning
| x | [6 empty] | 2006-06-01 |  | Man-3 |  |  | Commissioning - Building Tuning / Tenancy Fitout Tuning | Technical Clarification | 1 | Minimum quarterly (not monthly) reviews are required.
x | x | x | x | x | x |  | x | 2007-12-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | Technical Clarification | 2 | As this credit addresses tuning after handover, the evidence must clearly relate to that period (e.g. the timeline must go through the 12 month tuning process).
| x | x | x | x | x |  | x | 2011-01-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | Withdrawn | 3 | This clarification has been withdrawn. See Technical Clarification No. XX for more information. (Originally posted on Jun-08) This credit applies to all building systems. The scope includes the following systems: ventilation; heating; cooling; electrical; lighting; domestic hot water; mechanical. The scope is not limited to the systems above.
X | [7 empty] | 2009-07-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | CIR Ruling | 4 | Where the tenant and the base building owner are the same entity, the following documentation can be deemed equivalent to a copy of the tenancy fitout tuning contract as required by the technical manual. Projects seeking to use the following alternate documentation must demonstrate that both the tenant and the base building owner are the same entity. This can be demonstrated in the general section of the submission. The alternate documentation that can be submitted in this case is: - A copy of the extract(s) from the mechanical services specification that shows the scope and timeframe of the fitout tuning process (in accordance with the Credit Criteria); and - A copy of the extracts of the contract between the building owner/tenant and the building contractor that requires the contractor to undertake the actions detailed in the specification. Please ensure that the alternate documentation shows that the Credit Criteria and Compliance Requirements are being met.
x | x | x | x | x | x | x | x | 2011-01-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | Withdrawn | 5 | This clarification has been withdrawn. See Technical Clarification No. 6 for more information. (Originally posted on Jul-09) Lift services, fire services and hydraulic services should be excluded from this credit. However, a maintenance and tuning plan must be submitted for any systems for water collection, reuse, or recycling, on the project site.
x | x | x | x | x | x | x | x | 2011-01-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | Withdrawn | 6 | This ruling has been withdrawn as of 01-Nov-13. Please refer to Correction No. 9. Lift services, fire services and hydraulic services should be excluded from this credit. However, a maintenance and tuning plan must be submitted for any greywater and blackwater systems on the project site.
x | x | x | x | x | x | x | x | 2011-01-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning | Credit Interpretation Request | 7 | In cases where the building tuning has been completed prior to the Green Star As-built submission, letters from the different building services sub-contractors, rather than extracts from the contracts can be used to demonstrate compliance. The letter(s) must clearly show that all building systems within the building were tuned in accordance with all of the requirements in the Technical Manual.
[7 empty] | x | 2012-08-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning | Credit Interpretation Request | 8 | Tuning of building services is not required to take place within private dwellings.
|  | x | x | x | x | x | x | 2013-11-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning | Correction | 9 | The following services are exempted from the scope of this credit: * Lifts; * Fire services; and * Hydraulic services (wherever greywater and blackwater systems are not present); The following services must be addressed by the credit: * Greywater and blackwater systems. Please refer to the Technical Manual for all compliance and documentation requirements.
|  | x | x | x | x |  | x | 2009-03-01 | Man-3 | Man-3 | Man-3 | Man-3 | Commissioning - Building Tuning / Tenancy Fitout Tuning | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Project Timeline; and *Confirmation from the building owner. All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | X | X | X | X |  |  | Man-4 | Man-4 | Man-4 | Commissioning - Commissioning Agent
| x | x | x | x | x |  | x | 2008-01-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Independent Commissioning Agent | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem independent commissioning agent(s) sufficiently independent if they report directly to the building owner or the owner’s designated representative, even if they are paid by the contractor, is granted.
| x | x | x | x | x |  | x | 2008-04-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Independent Commissioning Agent | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to have an Independent Commissioning Agent appointed after the issuing of contract documentation, and to have such an Agent review and influence the workshop drawings, be deemed equivalent to the appointment of the Independent Commissioning Agent at design stage, and set the targets at contract documentation, is denied. This approach does not meet the intent of the credit.
| x | [6 empty] | 2008-10-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Independent Commissioning Agent | Correction | 3 | To align with the Compliance Requirements for Man-2 ‘Commissioning Clauses’, a “letter of commitment” will only be acceptable if the project has not commenced construction. Once construction has commenced, Credit Criteria cannot be met without an appointed Independent Commissioning Agent, so a “letter of appointment“ must be provided. (Applies to all projects registered from November 2008)
x | x | x | x | x | x | x | x | 2011-01-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Commissioning Agent | Technical Clarification | 4 | The role of the Independent Comissioning Agent (ICA) may be undertaken by either a single person or an organisation. When the role of the ICA is undertaken by an organisation, one person must have the overall responsbility for commissioing but that person may rely on the expertise of other staff within each discipline. It is noted that a copy of the CV for each of the people involved in the commissioning as well as evidence of each of their involvement in the commissioning process must be provided for assessment.
x | x | x | x | x | x | x | x | 2011-01-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Commissioning Agent | Technical Clarification | 5 | All of the commissioning tests do not need to be witnessed by the person with the overall responsibility but all commissioning must be carried out in accordance with the relevant ASHRAE/CIBSE standards and codes (when the Man-2 'Comissioning Clauses' credit is claimed), allowing the person with the overall responsibility to sign-off that the building systems have been commissioned.
X | X | X | X | X | X | X | X | 2013-11-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Commissioning Agent | Technical Clarification | 6 | The person or company providing ICA services to a project may change on the following conditions: * Each party is demonstrated to be a 'suitably qualified professional' in line with the compliance requirements of the credit; and * There is a comprehensive handover process between outgoing and incoming ICA. All other requirements outlined with the Technical Manual must be met. To demonstrate the above, the following documentation is required in addition to the documentation requirements outlined within the Technical Manual: * CVs for both ICA parties, in line with the documentation requirements of the credit. * Confirmation from incoming ICA that a handover process took place.
|  | x | x | x | x |  | x | 2009-03-01 |  | Man-4 | Man-4 | Man-4 | Commissioning - Commissioning Agent | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Proof of the independent commissioning agent’s involvement. In order to show involvement from the Independent Commissioning Agent (ICA), the "Extract(s) from the Commissioning Report" must contain a statement by the ICA that states the level of involvement in the project. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | X | X | X | X |  | Man-4 | Man-5 | Man-5 | Man-5 | Building Users' Guide / Tenant Guide
| x | [6 empty] | 2006-06-01 |  | Man-5 |  |  | Building Users' Guide / Tenant Guide | Technical Clarification | 1 | Compliance Requirements should read "A copy of the Building Users' Guide... OR A copy of a contract..."
[8 empty] | 2008-10-01 |  |  |  | Man-5 | Building Users' / Occupants Guide | Technical Clarification | M1 | A contract between the building owner/representative and the company commissioned to create the Building Users’ Guide can be submitted instead of the full Building Users' Guide provided that all the requirements of the Building Users’ Guide, as specified in the Man-5 credit of the Green Star – Office v3 Technical Manual, appear in the contract conditions.
x | x | x | x | x |  |  |  | 2008-12-01 | Man-4 | Man-5 | Man-5 | Man-5 | Building Users' / Occupants Guide | Technical Clarification | 2 | The GBCA publication ‘Clean Up Your Office Guide’, referenced within the Expansion/Re-fit Considerations section of the Compliance Requirements, is now published as ‘Clean Up Your Business Guide’. The use of either version of this document is acceptable.
x | x | x | x | x |  |  |  | 2008-12-01 | Man-4 | Man-5 | Man-5 | Man-5 | Building Users' / Occupants Guide | Technical Clarification | 3 | Simplified diagrams are aimed, and intended, for the use of the building occupants Simplified diagrams need to communicate the depicted service / system in a very basic and clear way that can be readily understood by the general public. Any drawing/diagram that contains technical detail does not generally fall into the category of a simplified diagram. Accordingly, construction drawings are not considered to be simplified diagrams.
| x | [6 empty] | 2009-04-01 |  | Man-5 |  |  | Building Users' Guide / Tenant Guide | Technical Clarification | 4 | In the Office Design v2 Technical Manual, the Compliance Requirements should read "A copy of the Building Users' Guide... OR A copy of a contract..."
[6 empty] | x |  | 2012-08-01 | Man-4 | Man-5 | Man-5 | Man-5 | Building Users' Guide / Tenant Guide | Technical Clarification | 5 | PILOT Projects: An Environmental Health and Mission Statement is not required to demonstrate compliance with this credit.
|  | x | x | x |  |  |  | 2009-03-01 | Man-4 | Man-5 | Man-5 | Man-5 | Building Users' Guide / Tenant Guide | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from the contract All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | X | X | X | X |  | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management
x | x | [6 empty] | 2007-12-01 | Man-5 | Man-6 |  |  | Environmental Management | Withdrawn | 1 | This Technical Clarification was withdrawn on May 2009. Please see Technical Clarification 7 and 8 for more information. Projects automatically qualify for full credit (3 points) if their EMS is certified under ISO-14001. Hence, projects qualify either for 2 points (without ISO-14001) OR for all 3 points (with ISO-14001). Once sufficient time has been allowed for organisations to obtain a more recent version of ISO-14001 certification, Green Star will require ISO-14001/2004 certification (not 1996). The contractor must have valid ISO14001 accreditation throughout the construction phase of the project. ISO 14001:2005 does not exist - only the abovementioned certification will be acceptable. Update: This CIR previously stated ISO-14001/2001 certification. It has been amended to reflect the proper ISO version ISO-14001/2004
|  | x | x |  |  |  |  | 2007-12-01 |  | Man-6 | Man-6 | Man-6 | Environmental Management | Technical Clarification | 2 | ISO 14001:2005 does not exist - only the certification stated in the Credit Criteria, or later will be acceptable.
|  | x |  |  |  |  | x | 2008-09-01 |  | Man-6 | Man-6 | Man-6 | Environmental Management | Technical Clarification | 3 | “Section 4 of the NSW Environmental Management System guidelines 1998 or 2007” (referenced in the Credit Criteria, Compliance Requirements and Additional Guidance) should read, “Section 4 of the NSW Environmental Management Systems Guidelines 1998 or Section 3 of the NSW Environmental Management System Guidelines 2007.”
[7 empty] | x | 2009-03-01 |  |  |  | Man-6 | Environmental Management | Technical Clarification / CIR Ruling / Correction | 4 | Where the principal building contract has not been awarded, project teams will be required to demonstrate compliance with the Credit Criteria for two points for provision of an Environmental Management Plan (EMP) by providing the following: - Extract from the tender documentation indicating the requirement for the head contractor and builders to provide and implement a comprehensive EMP for the works in accordance with Section 4 of the NSW Environmental Management System Guidelines 1998 or Section 3 of the NSW Environmental Management System Guidelines 2007.
|  |  | x | x | x |  | x | 2009-05-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | Technical Clarification | 5 | Projects are able to use Section 4 of the NSW Environmental Management System Guidelines (1998) as stipulated in the Technical Manual, or Section 3 of the NSW Environmental Management System Guidelines (2007).
x | x | x | x | x | x |  | x | 2009-07-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | CIR Ruling | 6 | The Credit Interpretation Request to deem an ‘Acknowledgement of Application’ notice for ISO14001 Certification equivalent to an ‘ISO 14001 certificate’ is denied as there is no equivalence between a document that acknowledges reception of documentation and a post audit official certificate. There is no guarantee that certification will be granted once the contractors EMS is audited.
| x | [6 empty] | 2011-01-01 |  | Man-6 |  |  | Environmental Management | Withdrawn | 7 | This clarification has been withdrawn. See Technical Clarification No. 13 for more information. (Originally posted on Jul-09) Projects automatically qualify for full credit (3 points) if their EMS is certified under ISO-14001. Hence, projects qualify either for 2 points (without ISO-14001) OR for all 3 points (with ISO-14001).
x | [7 empty] | 2011-01-01 | Man-5 |  |  |  | Environmental Management | Withdrawn | 7 | This clarification has been withdrawn. See Technical Clarification No. 14 for more information. (Originally posted on Jul-09) Projects automatically qualify for full credit (4 points) if their EMS is certified under ISO-14001. Hence, projects qualify either for 2 points (without ISO-14001) OR for all 4 points (with ISO-14001).
x | x | [6 empty] | 2009-07-01 | Man-5 | Man-6 |  |  | Environmental Management | Technical Clarification | 8 | The contractor must have valid ISO14001 accreditation throughout the construction phase of the project.
[6 empty] | x |  | 2009-10-01 |  |  |  | Man-6 | Environmental Management | CIR Ruling | I1 | A Final EMP Post Implementation Inspection Report is equivalent to the 'Confirmation from the Contractor' provided that: • A comprehensive, project-specific EMP is provided as per the provisions of the Credit Criteria and Compliance Requirements; and • The project team demonstrates that the EMP was implemented from the beginning of the construction and applied throughout the construction process of the building.
[6 empty] | x |  | 2009-10-01 |  |  |  | Man-6 | Environmental Management | CIR Ruling | I2 | The Credit Criteria ensures that the operations and activities of contractors and sub contractors are controlled to ensure sound environmental performance in line with ISO14001 accreditation. The fact that a consultant organisation that develops and supervises the implementation of an Environmental Management Plan has an ISO14001 certificate cannot be deemed equivalent to the actual requirement of the Credit Criteria.
x | [7 empty] | 2011-01-01 | Man-5 |  |  |  | Environmental Management | Correction | 13 | The points in this credit are independent of each other. A project team can claim 2 points for complying with the requirements of the Environmental Management Plan Criterion, or 2 points for complying with the ISO 14001 accreditation Criterion. A project can also claim 4 points for complying with both Criteria. Full points will not be automatically awarded for only complying with the ISO 14001 accreditation Criterion.
| x | [6 empty] | 2011-01-01 |  | Man-6 |  |  | Environmental Management | Correction | 14 | The points in this credit are independent of each other. A project team can claim 2 points for complying with the requirements of the Environmental Management Plan Criterion, or 1 point for complying with the ISO 14001 accreditation Criterion. A project can also claim 3 points for complying with both Credit Criteria. Full points will not be automatically awarded for only complying with the ISO 14001 accreditation Criterion.
x | [7 empty] | 2012-08-01 | Man-5 |  |  |  | Environmental Management | CIR Ruling | 16 | The Compliance requirement states that the following must be provided: - A copy of the ISO 14001 Certificate; - A copy of the management review minutes; and - A copy of internal audit reports. This may be replaced by the documentation requirements in Green Star - Office As-built v3 - Contractor ISO14001 certificate: A copy of the current and valid ISO14001 certificate; and, - Confirmation of Subcontractor adherence to ISO14001 requirements: Documentation included with the EMS or Project - EMP showing that any subcontractors relevant to the project were required to adhere to applicable ISO14001 requirements. It must be demonstrated that the ISO14001:2004 certification is applicable to the tenancy fitout works in order for the Certified Assessors to award points under this criterion
x | x | x | x | x | x | x | x | 2012-08-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | CIR Ruling | 17 | The Environmental Management Plan must be in accordance with either: - Section 4 of the NSW Environmental Management Systems Guidelines 1998; or - Section 3 of the NSW Environmental Management System Guidelines 2007; or - Section 3 of the NSW Environmental Management System Guidelines 2009.
x | [7 empty] | 2012-08-01 | Man-5 |  |  |  | Environmental Management | Technical Clarification | 18 | It is acceptable to provide an external audit report in place of the internal audit report to demonstrate compliance with ISO14001.
x | [7 empty] | 2012-08-01 | Man-5 |  |  |  | Environmental Management | Technical Clarification | 19 | The project team may show compliance with the second criterion of Man-5 Environmental Management; "2 points are awarded where it is demonstrated that the contractor had ISO 14001:2004 Environmental Management System certification for the tenancy fitout," by providing the following documentation in the submission: - Contractor ISO14001 certificate: A copy of the current and valid ISO14001 certificate; and, - Confirmation of Subcontractor adherence to ISO14001 requirements: Documentation included with the EMS or Project EMP showing that any subcontractors relevant to the project have adhered to applicable ISO14001 requirements. It must be demonstrated that the ISO14001:2004 certification is applicable to the tenancy fitout works in order for the Certified Assessors to award points under this criterion.
|  | x | x | x |  |  |  | 2009-03-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the contractor In order to show that the Environmental Management Plan (EMP) was implemented during construction works, the following must be provided instead. - Short Report describing how the EMP was implemented, including a summary table describing all the reporting created through the use of the EMP confirming its thorough implementation in accordance with Section 3 of the NSW Environmental Management System guidelines 2007; and - Compliance Matrix that includes the NSW Environmental Management System requirements and a statement of how these have been fulfilled. All other documentation must be provided as per the Technical Manual at the time of submission.
x | [7 empty] | 2012-08-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the contractor In order to show that the Environmental Management Plan (EMP) was implemented during construction works, the following must be provided instead. - Short Report describing how the EMP was implemented, including a summary table describing all the reporting created through the use of the EMP confirming its thorough implementation in accordance with Section 3 of the NSW Environmental Management System guidelines 2007; and - Compliance Matrix that includes the NSW Environmental Management System requirements and a statement of how these have been fulfilled. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2012-08-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | Documentation (Design) | C | The documentation requirements for a design submission has been updated as follows: Short report prepared by relevant project team member that demonstrates how the Credit Criteria has been met. Where the point for providing an EMP is claimed: Extract(s) from tender documents: - Specifying that a comprehensive, project specific EMP will be developed and implemented by the contractor; and - Specifying that the EMP will comply with the applicable requirements of the NSW Environmental Management System Guidelines Where the point for the contractor being required to have ISO 14001 accreditation is claimed Extract(s) from tender documents specifying that the contractor must have a current and valid ISO 14001 EMS in place prior and throughout construction works, and that a copy of the certificate is required to be included in their tender response.
x | x | x | x | x | x | x | x | 2013-11-01 | Man-5 | Man-6 | Man-6 | Man-6 | Environmental Management | Documentation (Design) | D | The following is an accepted alternative approach to demonstrating compliance with this credit at the time of a Green Star – Design: In lieu of providing: * Compliance Matrix confirming implementation of the Environmental Management Plan in accordance with Section 3 of the NSW Environmental Management Systems (EMS) Guidelines. Project teams can choose to provide: * The contractor’s accreditation certificate under the NSW EMS Guidelines.
x | x | x | x | X | X | X | X |  | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout
| x | [6 empty] | 2006-06-01 |  | Man-7 |  |  | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 1 | Asbestos or other hazardous materials that legally must be withheld from general construction waste do not have to be included in the calculation for the total waste by mass.
| x | [6 empty] | 2007-12-01 |  | Man-7 |  |  | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 2 | If a sub-contractor is engaged to sort and recycle construction waste on the project's behalf and does it on 'bulk' basis (not on a project basis), the credit can be claimed if the sub-contractor can provide evidence of diverting the claimed percentage of waste on average.
x | x | [6 empty] | 2007-12-01 | Man-6 | Man-7 |  |  | Waste Management / Waste Management During Tenancy Fitout | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to allow contractor(s) to measure waste by volume is granted, presuming that the results will be converted to mass for the purpose of Green Star submission (i.e. please submit for this credit in accordance with the Technical Manual). Please support the conversion factors chosen, and note that the Certified Assessor(s) will evaluate the veracity of the conversion process.
x | x | x | x |  |  |  |  | 2007-12-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 4 | As per the Credit Criteria, this credit addresses all project waste. For the purposes of this credit, this includes demolition and construction waste, but not soil or contaminated waste, as those would normally be excluded from the general waste stream.
x | x | x | x |  |  |  |  | 2008-01-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 5 | This credit applies to all waste from construction activities, including existing carpet and ceiling tiles. Please note that the Additional Guidance clearly identifies these materials as having the potential to be re-used / reconditioned or recycled.
x | x | x | x | x |  |  |  | 2008-01-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | CIR Ruling | 6 | The Credit Interpretation Request (CIR) to exclude the demolition waste associated with the demolition of the existing building(s) from the total amount of waste generated on the project from the credit requirements is denied, as this would contradict the current Credit Criteria.
x | x | x | x | x |  |  |  | 2008-03-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | CIR Ruling | 7 | The Credit Interpretation Request (CIR) to provide a letter from the building owner confirming that the contractor was required to carry out the waste recycling for a minimum fixed proportion of the waste by weight and report to the client, instead of an extract from the contract provision for a Green Star – As Built rating, is granted conditionally on the project’s ability to provide the following: - A short report detailing how the waste management activities were carried out in accordance with the Technical Manual, including the description of how the minimum fixed proportion of the waste by weight was recycled or reused; and - All other submitted documentation clearly demonstrating that the compliance requirements have been met. The Certified Assessor(s) will look for a similar level of certainty to that expected from a contractual provision.
| x | [6 empty] | 2008-12-01 | Man-6 | Man-7 |  |  | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 8 | There is a discrepancy within the Credit Criteria and Compliance Requirements with regards to the required frequency of reporting. The reporting must occur on at least on a 'quarterly' basis in order to comply with this Credit. Monthly reporting is also acceptable.
| x | [6 empty] | 2009-03-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Correction | 9 | Within the Additional Guidance section of the Green Star - Office As Built v2 Technical Manual, it should state "The Green Star - Office Design v2 Technical Manual provides guidance on what systems should be in place at the establishment of the project to facilitate the achievement of this credit."
|  | x | x | x | x | x | x | 2012-08-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Technical Clarification | 8 | In relation to the 'Extract(s) from the contract(s),' the requirement for "the exact provisions of the Credit Criteria must be found in the body (rather than Appendices) of the document," is removed. The full criteria need not be included in the main body of the contract so long as it is clearly demonstrated the full requirements of the credit are part of the contracted scope of works for the project. The project team may therefore submit the following: Extract(s) from the contract(s) between the contractor and either the developer or the building owner, stipulating the full criteria for re-use or recycling of the stated proportion of construction and demolition waste.
|  | x | x | x |  |  |  | 2009-03-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Waste Management Plan * Extract(s) from the contract(s) * Confirmation from the contractor All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | x |  |  |  | 2012-08-01 | Man-6 | Man-7 | Man-7 | Man-7 | Waste Management / Waste Management During Tenancy Fitout | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * An extract from the contract provisions which demostrates that the contractor was required to reuse/recycle a minimum fixed proportion of construction waste and report on waste reuse quarterly to the client All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  | x | [8 empty] | Man-8 | Waste Management-Operations Plan
|  |  | x |  |  |  |  | 2011-01-01 |  |  |  | Man-8 | Waste Management - Operations Plan | Correction | 1 | The manual refers to: 'Policy for Waste Minimisation in New Developments (NSW 2004). The reference should be: 'Policy for Waste Minimisation in New Developments' - Council of the City of Sydney (2005).
|  |  | x |  |  |  |  | 2012-08-01 |  |  |  | Man-8 | Waste Management - Operations Plan | Technical Clarification | 2 | It is acceptable to provide either of the following documents at the design stage of the project, instead of both as outlined in the Technical Manual: - The Waste and Recycling Management Plan, or - A contract reference for the project team to complete a Waste and Recycling Management Plan and to transfer to the owner upon building handover as per the Technical Manual.
|  |  | x |  |  |  |  | 2009-03-01 |  |  |  | Man-8 | Waste Management-Operations Plan | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Tenancy lease agreement * Extract(s) from specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  | x |  |  |  |  | 2009-03-01 |  |  |  | Man-8 | Waste Management-Operations Plan | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Extract(s) from the contract * Confirmation from the contractor All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  | x |  | x | [6 empty] | Man-9 | Building Management Systems
|  |  | x |  | x |  |  | 2009-03-01 |  |  |  | Man-9 | Building Management Systems | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Signed commitment from the owner. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x |  | x |  |  | 2013-11-01 |  |  |  | Man-9 | Building Management Systems | Documentation (As Built) | B | Where the facility manager for the project is an in-house employee of the project owner, the following documentation is no longer required at the time of a Green Star – As Built Submission: * Contract with the facilities manager Instead project teams must submit the following: * A letter of commitment from the building owner, which confirms adherence to the same points as the contract requirements outlined in the compliance requirements; and * Extract of facilities manager’s position description outlining the role of the facilities manager which must include the following in line with the requirements of the Credit: - In monitoring energy and water consumption and alarms in the BMS; and - Providing tenants with quarterly reports showing energy and water consumption from each sub-meter.
|  |  |  | x | [7 empty] | Man-10 | Learning Resource
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | Man-10 | Learning Resource | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | Man-10 | Learning Resource | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the contractor The following ADDITIONAL documentation is required to be submitted instead: * Confirmation from the school/school board indicating that all initiatives and display mechanisms have been installed. All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x | x | [6 empty] | Man-11 | Maintainability
[5 empty] | x | [6 empty] | Man-12 | Construction Indoor Air Quality Plan
[5 empty] | x | [6 empty] | Man-13 | Sustainable Procurement Guide
[12 empty] | Man-14 | Operations Environmental Management
[12 empty] | Man-15 | Precinct Environmental Management
[7 empty] | x |  |  |  |  | Man-16 | Metering
[7 empty] | x | 2011-01-01 |  |  |  | Man-16 | Metering | Technical Clarification | 2 | For Smart-metering: The following options are considered equivalent to Smart-metering : • BMS controlled metering for each dwelling that collects consumption data at least once every hour; or • On-line metering systems that collect consumption data at least once every hour. In each case, the metering system must also provide - a visual display of real time consumption data installed in an easlily accessible and visible location in each dwelling for use by the resident; and - a function to analyse data at regular intervals; and - a function that can present the financial costs and the greenhouse gas emissions associated with the usage.
[7 empty] | x | 2012-08-01 |  |  |  | Man-16 | Metering | Technical Clarification | 3 | The provision of an online metering system to display the electricity, gas, and water usage per dwelling is not an acceptable alternative to meet the aim of the credit as it cannot be demonstrated that this provides an equivalent degree of accessibility and visibility to a wall-mounted display, which is continuously visible and available to the dwelling occupant.
[7 empty] | x | 2012-08-01 |  |  |  | Man-16 | Metering | Technical Clarification | 4 | The installation of energy and water authority meters for each dwelling, and the use of the authority quarterly billing process is not sufficient to meet the intent of the credit. It is clearly stated that in addition to the installation of meters, an effective mechanism to monitor energy and water consumption data must be in place. An effective mechanism to monitor energy and water consumption data must allow for the collection of daily usage data as a minimum.
[7 empty] | X | 2013-11-01 |  |  |  | Man-16 | Metering | Technical Clarification | 5 | For Smart Meters to demonstrate ‘real time’ consumption, they must have the capacity to report metering data every 15 minutes as a minimum. Reporting frequencies of greater than 15 minutes (e.g. Every minute or every 5 minutes) are also deemed compliant.
[7 empty] | X | 2013-11-01 |  |  |  | Man-16 | Metering | Technical Clarification | 6 | The following is deemed to meet the requirement for smart metering for gas: *a pulse meter which shows consumption of gas every 15 minutes (or more frequently) and is connected to a visual display as outlined within the Credit Criteria.

## IEQ (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Indoor Environment Quality
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering |  |  | Ov2
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | IEQ-0 | IEQ-0 | IEQ-0 | IEQ-0 | General
| x | [6 empty] | 2008-09-01 |  | IEQ-0 |  |  |  | Withdrawn | 1 | If a paint (regardless of whether it is classified for interior or exterior applications) is applied on an internal surface, it must be included in the calculations for the 95% of all painted surfaces if the project wishes to claim the credit.
x | x | x | x | x | x | x | x |  | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates
| x | [6 empty] | 2006-06-01 |  | IEQ-1 |  |  | Ventilation Rates | Technical Clarification | 1 | The second item under Compliance Requirements for mechanically ventilated buildings should read: "A copy of the section of the mechanical specification where the minimum outside-air rate for the system is stipulated and where design occupant density is specified". The same occupancy density must be used throughout the submission unless otherwise specified in Compliance Requirements (i.e. for Wat-1, Ene-1 or Ene-2).
| x | [6 empty] | 2006-06-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 2 | Supplementary outside air systems can be incorporated into IEQ-1. However, the GBCA does not expect many projects to utilise Supplementary O/A systems in IEQ-1 because: 1. The system would have to be operating whenever the air conditioning system is operating (as the Credit Criteria states "Up to 3 points are awarded if minimum outside air is PROVIDED at rates..." (not potentially available). In addition, AS1668.2 would also require the system to be operational. It is NOT sufficient just to have system available for the tenant to connect to.
| x | [6 empty] | 2006-06-01 | IEQ-1 | IEQ-1 | IEQ-1 |  | Ventilation Rates | Technical Clarification | 2 | 2. The supplementary system must be installed and operated (including energy and maintenance) by the base-building, similar to the way that supplementary cooling towers and pumps are operated by the base building. The only exception Green Star allows to this rule is for office lighting (which is generally installed by base building but operated by the tenants), yet it will assess both the environmental benefit and energy penalty on the tenant in High Frequency Ballasts (IEQ-6/IEQ-12), Electric Light Levels (IEQ-7/IEQ-13), Lighting Power Density (Ene-3/Ene-5) and Lighting Zoning (Ene-4), and therefore counteracts claiming environmental benefits without also considering any detrimental impact.
| x | [6 empty] | 2006-06-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 2 | 3. The supplementary system must be installed and operated (including energy and maintenance) by the base-building, similar to the way that supplementary cooling towers and pumps are operated by the base building.
x | x | x | x | x | x |  | x | 2007-08-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 3 | Please be reminded that inclusion of supplementary outside air systems in IEQ may have a detrimental impact on other Green Star credits, such as Thermal Comfort (IEQ-5/IEQ-9). The Certified Assessor(s) are required to assess the coordination between credits.
x | x | [6 empty] | 2007-08-01 | IEQ-1 | IEQ-1 |  |  | Ventilation Rates | Technical Clarification | 4 | Although there is perceived discrepancy between IEQ-1 'Ventilation Rates' and Section J of the BCA, this is not the case. Projects cannot use the Deemed-to-Satisfy provisions of the BCA should they chose to claim IEQ-1 'Ventilation Rates'. Demonstration of compliance by verification method should be used.
| x | x | x | x | x |  | x | 2007-01-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to deem an increased outside-air solution that relies on the operation and adjustment by the facility management to achieve desired performance as providing an alternative yet equivalent level of compliance with the Aim of the Credit is denied - Green Star assesses building attributes and rewards them for ensuring a superior environmental outcome regardless of future operations.
[8 empty] | 2008-09-01 |  |  |  | IEQ-1 | Ventilation Rates | Technical Clarification | M1 | The trickle ventilation inlets must be operable.
[8 empty] | 2008-09-01 |  |  |  | IEQ-1 | Ventilation Rates | Technical Clarification | M2 | The effective total opening area of all trickle inlets must be 0.05% of floor area. Project teams should also refer to the requirements of the BCA and the Australian Standards for vent opening installation.
x | x | [6 empty] | 2008-12-01 | IEQ-1 | IEQ-1 |  |  | Ventilation Rates | Correction | 6 | Projects seeking to claim IEQ-2 ‘Carbon Dioxide Monitoring and Control’ must use the following reference set points (in parts-per-million): • 800 PPM for 50% increase; • 700 PPM for 100% increase; and • 640 PPM for 150% increase
|  |  |  | x | x |  |  | 2009-12-01 |  |  |  | IEQ-1 | Ventilation Rates | Technical Clarification | 7 | This clarification was modified to include additional tools. (originally posted Jul-09) The 'Not Applicable' (na) option, and the reference to 'open mall areas', in a number of Green Star Technical Manuals for this credit is an error. These references only apply to the Green Star - Retail Centre v1 rating tool.
| x | x | x | x | x | x | x | 2009-10-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 8 | Where the occupant density is unknown, in order to claim a percentage increase over AS1668.2, projects must demonstrate that they have improved based on the occupancy rates prescribed within Table A1 Appendix A of the same standard, not on different, or lower, tenancy figures.
x | [7 empty] | 2012-08-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 9 | This ruling clarifies the requirements of the Technical Manual. It must be demonstrated that the increased flow rates must be provided for 90% of the NLA. This is the total NLA of the tenancy, including meeting rooms. The summary document required as per dot point three on page 2 of 4 of the Technical Manual must demonstrate whether or not each space served by an AHU meets the Credit Criteria.
|  |  |  | x |  |  |  | 2012-08-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Technical Clarification | 10 | Where the Technical Manual refers to the ‘Engineered Procedure based on the Dilution Index’ from AS1668.2-1991, this is an error. The reference should be to the ‘Engineered Procedure based on the Dilution Index’ from AS1668.2-2002.
|  |  | x |  |  |  |  | 2013-11-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Correction | 11 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Ventilation Rates | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: For Naturally Ventilated Spaces: * Extract(s) from the Commissioning Report Provided that no automation controlling the flow of natural ventilation, such as automated louvres, has been provided. All other documentation must be provided as per the Technical Manual at the time of submission.
x | [7 empty] | 2011-01-01 | IEQ-1 | IEQ-1 | IEQ-1 | IEQ-1 | Alteration Point | Technical Clarification | 9 | The ‘Alteration Credit’ is ‘Not Applicable’ when zero points are awarded in the Credit Criteria.
| x | x | x | x | x | x | x |  |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness
| x | x | [5 empty] | 2008-12-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem this Credit ‘Not Applicable’ where a project is being delivered as a shell and core project is denied. This change would alter default values used by all projects, jeopardising equitable assessment and disadvantaging projects that have already obtained their rating.
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | IEQ-2 | Air Change Effectiveness | Technical Clarification | 2 | The nominated area for the deemed to satisfy criteria is the NLA of the BCA Class 5 component of the project
| x | x | x | x | x |  | x | 2009-04-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem the use of workstation-based air delivery systems equivalent to providing floor diffusers at least every 20m2, is granted conditionally on the project’s ability to clearly demonstrate all of the following: - The workstation-based solution must be provided and paid for by the base building owner/developer (cost-share is appropriate if agreed to by both the tenant and the owner, if different); - The workstation-based solution must be fully installed and operational (commissioned if recommended by the supplier or the design team) prior to occupancy; The submission must include a project-specific short report by the relevant professional that clearly describes and justifies the effectiveness of the air supply system, referencing and appending any relevant evidence that is provided within the submission. The Certified Assessor(s) will not award this Credit if it has not been clearly demonstrated that the alternative solution is at least as equally effective in meeting the Aim of the Credit and that the evidence is presented clearly in the submission.
|  |  |  | x | x |  |  | 2009-12-01 |  |  |  | IEQ-2 | Air Change Effectiveness | Technical Clarification | 4 | This clarification was modified to include additional tools. (originally posted Jul-09) The 'Not Applicable' (na) option, and the reference to 'open mall areas', in a number of Green Star Technical Manuals for this credit is an error. These references only apply to the Green Star - Retail Centre v1 rating tool.
|  |  |  | x |  |  |  | 2011-01-01 |  |  |  | IEQ-2 | Air Change Effectiveness | Correction | 5 | In the technical manual, short reports for Design and As-Built are described on pages 67 and 69. The fourth paragraph states: ‘Where the credit is claimed as ‘not applicable’, providing calculations that demonstrate that ‘open air mall’ areas make up more than 95% of the project’s total common areas.’ This paragraph should be disregarded. Claiming that this credit is 'not applicable' is not an option in certification submissions for Green Star - Education v1.
|  |  | x |  |  |  |  | 2013-11-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Correction | 6 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Documentation (Design) | A | Tender Architectural Drawings, required at the time of a Green Star - Design submission, can be substituted by the following documentation: * Tender Drawings Provided that these contain the same level of information as that which is required in the Technical Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: For Naturally Ventilated Spaces: * Extract(s) from the Commissioning Report All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Documentation | C | The key summary from either the airflow simulation report (for naturally ventilated spaces) or the CFD report (for mechanically ventilated spaces) can be submitted instead of the Short Report, provided that the key summary has been prepared by a suitable professional and describes how the credit criteria has been met by: * Describing the proposed system; * Including a tabulated summary table that identifies all spaces in the building and their area, nominates compliant spaces, indicates their ventilation mode and how compliance is achieved and confirms that compliant spaces jointly account for at least the stipulated proportion of the nominated area; and * For naturally ventilated spaces, referencing either the schedule of openings, the empirical calculations or the computer modelling report and demonstrating that the building is designed as a naturally ventilated space in accordance with AS1668.2 2002, and describing the key elements of the natural ventilation system and the sequence of operations, which must be clearly shown in easy to read diagrams or sketches.
X | X | X | X | X | X | X |  | 2013-11-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Documentation (Design) | D | Based on feedback from assessors and project teams, the GBCA is releasing the following documentation approach for IEQ-2 Air Change Effectiveness. This is one acceptable approach to demonstrating compliance with this credit, project teams may choose to demonstrate compliance with the documentation outlined in the Technical Manual if they choose to do so. Documentation Pathway - Design In lieu of all documentation outlined within the Technical Manual (including the CFD Modelling Report), project teams may provide: • A letter from the Mechanical Engineer responsible for design of HVAC systems which (please refer to the template letter available from the GBCA website): - Describes the way in which the HVAC systems have been designed to deliver a uniform distribution of ventilation and to avoid short circuiting of airflow delivery to occupied spaces within the building; and - Explains, in qualitative terms, how the above has been achieved to all occupied spaces. In relation to ventilation of occupied space commentary must cover distribution of supply air diffusers and return air points/paths, location of return air points in relation to supply air, how potential for short circuiting is mitigated, appropriate diffuser selection, supply air temperature and velocity in heating and cooling modes; and - Identifies any spaces that are not mechanically air conditioned and also identifies mechanically air conditioned spaces that do meet the above criteria. -AND- • The CV of the Mechanical Engineer detailing relevant qualifications and experience. Please note that this ruling is an interim solution. The GBCA is currently reviewing and seeking feedback on alternative methods for the assessment of Air Change Effectiveness for Design and As-Built submissions.
X | X | X | X | X | X | X |  | 2013-11-01 |  | IEQ-2 | IEQ-2 | IEQ-2 | Air Change Effectiveness | Documentation (As Built) | E | Based on feedback from assessors and project teams, the GBCA is releasing the following documentation approach for IEQ-2 Air Change Effectiveness. This is one acceptable approach to demonstrating compliance with this credit, project teams may choose to demonstrate compliance with the documentation outlined in the Technical Manual if they choose to do so. Documentation Pathway - As Built In lieu of all documentation outlined within the Technical Manual (including the CFD Modelling Report), project teams may provide: • A letter from a qualified Mechanical Engineer involved in the project during construction and commissioning of HVAC systems which (please refer to the template letter available from the GBCA website): - Describes the way in which the HVAC systems have been designed, constructed and commissioned to deliver a uniform distribution of ventilation and to avoid short circuiting of airflow delivery to occupied spaces within the building; and - Explains, in qualitative terms, how the above has been achieved to all occupied spaces. In relation to ventilation of occupied space commentary must cover distribution of supply air diffusers and return air points/paths, location of return air points in relation to supply air, how potential for short circuiting is mitigated, appropriate diffuser selection, supply air temperature and velocity in heating and cooling modes; and - Identifies any spaces that are not mechanically air conditioned and also identifies mechanically air conditioned spaces that do meet the above criteria; and - Confirms that all relevant systems have been commissioned in line with documented design using a relevant commissioning code (ASHRAE, CIBSE or AIRAH), listing the commissioning code(s) used to guide the commissioning process. -AND- • The CV of the Mechanical Engineer detailing relevant qualifications and experience. Please note that this ruling is an interim solution. The GBCA is currently reviewing and seeking feedback on alternative methods for the assessment of Air Change Effectiveness for Design and As-Built submissions.
x | x | x | x | x | x | x |  |  | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control
| x | [6 empty] | 2006-01-01 |  | IEQ-3 |  |  | Carbon Dioxide Monitoring and Control | Technical Clarification | 1 | If credit is claimed under IEQ-1 'Ventilation Rates', the minimum threshold must correlate to rate claimed in IEQ-1. The occupant density referenced for ventilation credits must be consistent with the design occupant density stipulated in the mechanical services specification.
| x | [6 empty] | 2007-01-01 |  | IEQ-3 |  |  | Carbon Dioxide Monitoring and Control | Technical Clarification | 2 | Carbon Dioxide (CO2) sensors must be located at all return air points on each floor (usually ducts) - location purely within risers does not support the Aim of the Credit. Location within return ducts only or within return ducts and return risers is acceptable.
x | [7 empty] | 2007-12-01 | IEQ-2 |  |  |  | Carbon Dioxide Monitoring and Control | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem the installation of CO2 sensors in office areas only equivalent to their installation in all return air ducts, for all enclosed spaces less than 100m2, is denied because the outside air supplied to other tenancy areas from the same duct is not controlled.
x | [7 empty] | 2008-01-01 | IEQ-2 |  |  |  | Carbon Dioxide Monitoring and Control | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to meet the Credit Criteria by installing, within each enclosed space that is less than 100m2, a combination of a wall-mounted CO2 sensor linked to a BMS system and a VAV box that supplies outside air to that space is granted conditionally on the project’s ability to demonstrate that: - The CO2 sensors are able to control the volume of outside air that is provided to the enclosed spaces; - The quality of the air and the temperature settings within the enclosed space will not be compromised by the CO2 sensors operating the VAVs; - Any impact that these proposed strategies will have on related credits (such as energy consumption) is reflected consistently throughout the submission; - The quality of air and temperature supplied to other spaces within the same duct is not compromised when a CO2 sensor within a space activates the VAV system. See the Technical Clarifications section of the GBCA website for additional information on this point;
x | [7 empty] | 2008-01-01 | IEQ-2 |  |  |  | Carbon Dioxide Monitoring and Control | CIR Ruling | 4 | - Any assumptions made with regards to the operation of this system are justified in a conservative and robust way throughout the submission; - The Aim of Credit has been clearly met; and - All of the documentation is as-built/as-installed in strict accordance with the Green Star – Office Interiors v1.1 Technical Manual.
x | x | [6 empty] | 2008-12-01 | IEQ-2 | IEQ-3 |  |  | Carbon Dioxide Monitoring and Control | Technical Clarification | 5 | Projects seeking to claim this credit with IEQ-1 ‘Ventilation Rates’ can use the carbon dioxide control system to reduce outside air rates in periods of low occupancy. Where this is the case, projects must use the following reference set points (in parts-per-million): • 800 PPM for 50% increase; • 700 PPM for 100% increase; and • 640 PPM for 150% increase
x | x | x | x | x | x | x |  | 2009-04-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | Technical Clarification | 6 | For mechanically air-conditioned and mechanically assisted naturally ventilated spaces, the outside air quantity set points and operational modes (as per the Additional Guidance) must be clearly indicated in the short report.
x | [7 empty] | 2009-07-01 | IEQ-2 |  |  |  | Carbon Dioxide Monitoring and Control | CIR Ruling | 7 | The Credit Interpretation Request (CIR) to deem the installation of one CO2 sensor in the plant room equivalent to the credit criteria is denied. This credit addresses the need for enclosed spaces to have appropriate levels of outside air based on the CO2 levels of the room. The approach proposed by this CIR has not been shown to be equivalent to the Credit Criteria, or the Aim of Credit.
|  |  |  | x | x | [6 empty] | IEQ-3 | Carbon Dioxide Monitoring and Control | Technical Clarification | 8 | This clarification was modified to include additional tools. (originally posted Jul-09) The 'Not Applicable' (na) option, and the reference to 'open mall areas', in a number of Green Star Technical Manuals for this credit is an error. These references only apply to the Green Star - Retail Centre v1 rating tool.
[8 empty] | 2009-10-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | CIR Ruling | p | A system that allows air to be recirculated during warmup mode can still achieve the credit providing the system: - Provides 100% outside air during working hours; and - A commitment to not modify the amount of outside air being provided during operating hours exists from the building owner, and is part of the O&M manual. The following documentation is required to demonstrate compliance must be submitted for projects using similar systems at the the time of submission: - Short Report describing the mechanical ventilation system in place and describing how the credit criteria is achieved. In particular address in the report the measures taken to ensure the system does not have recirculation capability (except during the morning start-up mode) that could be switched on in the future as per Additional Guidance; - Drawings or schematics of the design showing the ventilation system layout. - Extracts from the mechanical or BMS specification(s) (Design) describing the operation of the mechanical system and outlining the proposed measures to ensure that 100% fresh air is delivered at all times except for morning start up. At a minimum the specifications must: - Define the morning start-up cycle in the BMS. - Delineate how the BMS will prevent, via software, the activation of the morning start up cycle when the building is occupied; and; - Require the duct and air handling system to be commissioned such that it is only possible to operate in full fresh air (occupied periods) or full return air (morning warm up) configurations. No partial configuration will be available via the BMS software. - Extract(s) from the Commissioning Report (As Built) describing the operation of the mechanical system and outlining the proposed measures to ensure that 100% fresh air is delivered at all times except for morning start up. At a minimum the extract(s) must: - Define the morning start-up cycle in the BMS. - Delineate how the BMS will prevent, via software, the activation of the morning start up cycle when the building is occupied; and; - Describe how the system has been designed and commissioned to operate in full fresh air (occupied periods) or full return air (morning warm up) configurations. No partial configuration will be available via the BMS software.
|  |  |  | x |  |  |  | 2011-01-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | Correction |  | Credit Criteria' in the technical manual must be replaced with the following: Naturally Ventilated Spaces One point is awarded where it is demonstrated that at least 95% of the nominated area is 'Naturally Ventilated’ as per IEQ-1 'Ventilation Rates' with ventilation rates directly controlled by occupants. Air Conditioned and Mechanically Assisted Naturally Ventilated Spaces One point is awarded where it is demonstrated that at least 95% of the nominated area has HVAC systems that provide 100% outside air with no recirculated component. -OR- One point is awarded where it is demonstrated that at least 95% of the nominated area has both of the following: – A VOC monitoring system with a minimum of one sensor per return air point. The VOC monitoring system must: ~ Be linked to the Building Management System; ~ Facilitate the continuous monitoring of VOC pollutants; and ~ Detect and provide an alarm when VOC pollutants reach 0.5 mg/m3 level. – A carbon dioxide (CO2) monitoring and control system with a minimum of one CO2 sensor at all return air points The CO2 Monitoring & Control system must: ~ Continuously monitor a space; and ~ Adjust the outside air ventilation rates based on the space conditions. Mixed-Mode Ventilated Spaces One point is awarded where it is demonstrated that spaces meet the Credit Criteria for Naturally Ventilated Spaces as well as the Credit Criteria for Air Conditioned and 'Mechanically Assisted Naturally Ventilated spaces. The 'nominated area' for this credit is Usable Floor Area (UFA), excluding external covered areas.
|  | x | x | x | x | x |  | 2009-03-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is naturally ventilated and meets the requirements of IEQ-1 'Ventilation Rates', this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  |  |  | x | x |  |  | 2011-01-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | Correction |  | The Compliance Requirements of this credit read: The VOC Monitor The VOC monitor is to provide for monitoring and alarm for VOC pollutants and should not be linked to the adjustment of outside air rates. The correct wording is: The VOC Monitor The VOC monitor is to provide for monitoring and alarm for VOC pollutants. It is not required that it be linked to the adjustment of outside air rates
|  |  | x |  |  |  |  | 2013-11-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | Correction | 9 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
|  | x | x | x | x |  |  | 2009-03-01 | IEQ-2 | IEQ-3 | IEQ-3 | IEQ-3 | Carbon Dioxide Monitoring and Control | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: For systems that provide 100% outside air, and there is no capacity for recirculation * Extracts from the Commissioning Report Where the system has the capacity for recirculation, the Extract(s) from the specifications must be provided. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x |  | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight
| x | [6 empty] | 2007-01-01 |  | IEQ-4 |  |  | Daylight | Withdrawn | 1 | See Technical Clarification No.4 Green Star - Office Design v2 and Green Star - Office As Built v2 stipulate that calculations be based on the Uniform Design Sky. If the software used for the calculations does not have a preset option for the Uniform Design Sky, it must be set up manually.
| x | [6 empty] | 2007-01-01 |  | IEQ-4 |  |  | Daylight | Technical Clarification | 2 | A Uniform Design Sky represents a sky with a constant value of luminance. Thus, no matter where in the sky you look, the model has the same value. Design Sky values are derived from a statistical analysis of outdoor luminance levels. They represent a horizontal luminance level that is exceeded 85% of the time between the hours of 9am and 5pm throughout the working year. Thus they also represent a worst-case scenario that you can design to and ensure your building will meet the desired light levels at least 85% of the time.The resulting semi-hemispheric 'bubble' is located at 'infinite' distance, therefore the shading effect of the immediate surrounding building will still be taken into account. Please note that the uniform sky distribution and diffuse luminance levels tend to vary from the equator to the poles.
| x | x | x | x | x |  | x | 2008-01-01 |  | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Technical Clarification | 3 | For all Green Star assessments, only base-building installed partitions (e.g. load bearing walls) must be included - tenant-installed/fitout partitions should not be included in the modeling/calculations.
x | x | x | x | x | x |  | x | 2008-01-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to allow the use of Overcast Sky for modelling rather than the Uniform Sky (as stipulated in the Technical Manual) is granted. Projects are advised that Daylight Factor calculations using a uniform design sky will produce results which are higher than those calculated using an overcast sky for typical facades. While the GBCA will accept the results from a model using an overcast sky, the GBCA will not consider a change in the benchmarks for this credit.
| x | [6 empty] | 2008-04-01 |  | IEQ-4 |  |  | Daylight | Technical Clarification | 5 | For IEQ-4 ‘Daylight’, IEQ-7 ‘Electric Lighting Levels’ and Ene-5 ‘Lighting Power Density’ where the values for the surface reflectance are unknown, the standard values for modelling these credits must be in accordance with AS1680.1-1990. The GBCA has previously recognised the following reflectance values as acceptable: 0.2 (floor), 0.5 (walls) and 0.8 (ceilings).
| x | x | x | x | x |  | x | 2008-08-01 |  | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Technical Clarification | 6 | Projects may choose to model and submit a report for typical floors of their project, rather than for a number of identical floors. Projects that choose to do so must justify that the selected floorplates represent the ‘worst case’ scenario amongst the floors they represent (incl. overshadowing by adjacent buildings). The Certified Assessor(s) reserve the right to request further clarification or justification to ensure that the project meets the Aim of the Credit.
| x | x | x | x | x |  | x | 2008-12-01 |  | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Technical Clarification | 7 | As-Built projects that have been previously awarded points for these credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credit (i.e. same shape floor plan, same glazing propoerties and floor-to-ceiling height) can submit a letter from the relevant consultant in place of an as-built model (the as-built drawings must still be provided). The letter must describe the extent of any changes and state the maximum impact they may have on the building performance if it were remodelled. In this case the number of points achieved in the Design rating will automatically be awarded. Please note: Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Modelling must account for worse case scenario; please see the assumptions clarification for more information.
|  | x | [5 empty] | 2009-04-01 |  |  | IEQ-4 | IEQ-0 | Daylight | Correction | 8 | The example provided in the Additional Guidance (page 69) should read as follows: "In this instance, wherever the internal light levels are 250 lux, the Daylight Factor is 2.5% and NOT 2.0%"
x | [7 empty] | 2009-07-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | CIR Ruling | 9 | The Credit Interpretation Request to demonstrate compliance by calculating the Daylight Illuminance be deemed equivalent to calculating the Daylight Factor is granted. To demonstrate compliance with the Credit Criteria, the percentage of work settings must have a Daylight Illuminance of at least 250 Lux.
[8 empty] | 2011-01-01 |  |  |  | IEQ-4 | Daylight | Technical Clarification | 10 | Atrium areas must be excluded from the Nominated Area calculations for the IEQ-4 Daylight credit.
| x | [6 empty] | 2012-08-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Technical Clarification | 11 | As Built Projects. The glazing receipts required by the documentation requirements, do not need to show costs. The costs may be blacked out, provided that the glazing receipts show the required details as per the Technical Manual (e.g. glazing type, quantities, etc). Alternatively, In lieu of the glazing reciepts required, the project team may provide both of the following pieces of documentation: - Statement from supplier confirming that the nominated type and quantity of glass was supplied for installation on site; and - Statement from Head or Sub-Contractor confirming the type and quantity of glass that was supplied and installed.
[7 empty] | x | 2013-11-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Correction | 12 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
x |  | x |  | x |  |  |  | 2013-11-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Technical Clarification | 13 | The GBCA has released the 'Green Star Daylight Hand Calculation Guide' which can be used to demonstrate compliance with the Green Star Daylight credit found within this tool. Please refer to the guide for more information.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Documentation (Design) | A | Projects can substitute Isometric Façade, Roof, Plan, and Site Plan drawings with Architectural Façade, Roof, Plan, and Site Plan drawings, provided that all the information required in the Technical Manual has been included within.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-3 | IEQ-4 | IEQ-4 | IEQ-4 | Daylight | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the supplier(s) * Confirmation from the Contractor Projects must submit the following documentation instead: * Confirmation from the Head Contractor identifying that the glazing was installed as per the drawings, and correlating the type of glazing installed against the information from the As Built Drawings and Material Data Sheets from the manufacturer. Furthermore, projects can substitute As Built Isometric Façade, Roof, Plan, and Site Plan drawings with As Built Architectural Façade, Roof, Plan, and Site Plan drawings, provided that all the information required in the Technical Manual has been included within. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x |  | x | x | x |  |  | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control
| x | [6 empty] | 2006-01-01 |  | IEQ-5 |  |  | Daylight Glare Control | Technical Clarification | 1 | It is the intent of the credit to bring glare control into the realm of owner's/developer's responsibility because research proves conventional internal blinds marginally effective. Hence it is required to install fixed or automated (with manual override) shading, as stipulated in the Technical Manual. If shading devices are present, they must be included in the daylight modeling if IEQ-4 'Daylight' credit is claimed.
| x | [6 empty] | 2006-01-01 |  | IEQ-5 |  |  | Daylight Glare Control | Technical Clarification | 2 | The area which is required to comply with this credit is the NLA (not GFA) of a project
| x | [6 empty] | 2006-09-01 |  | IEQ-5 |  |  | Daylight Glare Control | CIR Ruling | 3 | A project registered for v1 can claim IEQ-5 in accordance with Green Star - Office Design v2, but must adhere to the requirements fully, not selectively.
x | [7 empty] | 2007-12-01 | IEQ-4 |  |  |  | Daylight Glare Control | CIR Ruling | 4 | The Credit Interpretation Request(CIR) to deem a solution (consisting of a monitor that can pivot back and forth on a stand) as compliant with the intent of the credit is denied because the solution does not provide an equivalent measure of adjustability. Specifically, the monitor cannot be moved 50cm vertically, and it cannot be moved this distance horizontally without due preparation by the user (i.e. clearing the work surface).
| x | [6 empty] | 2008-01-01 |  | IEQ-5 |  |  | Daylight Glare Control | Technical Clarification | 5 | The Credit Criteria can be met through a combination of compliant fixed shading devices and automated internal blinds.
| x | x |  | x | x |  |  | 2008-03-01 |  | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Technical Clarification | 6 | Existing adjacent buildings can be used to determine whether the shading requirement is being met. The project must justify any assumptions regarding the calculations in their submission (i.e. by providing aerial photographs and elevations indicating the location, height and material (wherever relevant) of the surrounding structures).
x | [7 empty] | 2006-09-01 | IEQ-4 |  |  |  | Daylight Glare Control | Technical Clarification | 7 | Only one monitor per 18m2 needs to comply with the Credit Criteria for monitor arms; all others can be anything else. The GBCA intends to review this credit for the subsequent version of the rating tool.
x | [7 empty] | 2008-04-01 | IEQ-4 |  |  |  | Daylight Glare Control | CIR Ruling | 8 | The Credit Interpretation Request (CIR) to deem the provision of laptops equivalent to providing flat-screen monitors with an adjustable arm is granted conditionally on the project’s ability to demonstrate that the laptops, laptop stands, the laptop docking stations, or similar facilities, are not fixed to the desk. Where any of these are provided, they must provide the same amount of flexibility as the monitor arm, or a free standing laptop. Any additional monitor must meet the requirements for this credit. Please ensure that the design described for this credit is consistent with the Energy Modelling Report.
x | [7 empty] | 2008-08-01 | IEQ-4 |  |  |  | Daylight Glare Control | Technical Clarification | 9 | Only one monitor per 18m2 needs to be fitted with monitor arms to comply with the Credit Criteria. For example, if you were to have a 1000m2 fitout then: 1000m2 /18m2= 56 monitor arms - If such fitout were designed to have 76 workstations, then only 56 of those must meet the Compliance Requirements. - If the fitout was designed to have 50 workstations, then all those workstations must meet the Compliance Requirements. The distribution of monitor arms is limited to the workstations only. Meeting rooms, training rooms and other locations that are not regularly occupied are not addressed by the Credit Criteria even if the amount of monitor arms required by this credit exceeds the number of workstations. So as per our previous example, if the fitout was designed to have 50 workstations, plus a training room with 20 computers, then none of the computers in the training room would be required to have monitor arms.
x | x | x |  | x | x |  |  | 2008-12-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | CIR Ruling | 10 | The Credit Interpretation Request (CIR) to deem the combination of tinted glazing and fixed shading devices, which are shown to be effective via a daylight glare model, equivalent to the credit criteria, is granted conditionally on the project’s ability to demonstrate that the solution, as designed and built, will result in a reduction of glare to the user equivalent to that which is stated in the credit criteria. Projects must submit a CIR that shows how the specific solution is equivalent to meeting the Credit Criteria. The documentation submitted with the CIR must show: - The methodology used to create the daylight glare model and the software used; - How the selected points represent the areas that would be effected by glare; - That all terms are clearly defined within the report; - The Name, type, glazing properties, and location of glazing (please ensure that this is clear); and - How the results in the model are equivalent to that of the Credit Criteria in the Technical Manual. Projects using this methodology must show that the above requirements are met in the documentation. Please ensure that all documentation is clearly correlated and highlighted.
x | x | x |  | x | x |  |  | 2008-12-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | CIR Ruling | 11 | The Credit Interpretation Request (CIR) to deem the representation of Daylight Glare Control results as the percentage of the working plane area that is shaded, calculated once per month on the 21st, equivalent to stereographic diagrams, is granted conditionally on the project’s ability to demonstrate the following: - Visual images of modelled building from all four elevations (direct output from modelling software only). - Summary table of hours of penetration for all façades showing hours in the year affected by solar penetration as a minimum split into summer, winter and mid season showing every hour of working day. - Simple suncast images showing sun penetration of a typical floor plate for conditions nominated above. Projects using this methodology must show that the above requirements and the credit criteria are met in their submission documentation. Certified Assessors will be looking to ensure that the report reflects these items.
x | x | x | x | x |  |  |  | 2009-02-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Correction | 12 | The requirement to eliminate all direct sun penetration for this credit is being modified. Where the credit states "eliminate all direct sun penetration" it should be interpreted as "eliminate 95% of all direct sun penetration". This change accounts for the need to allow a small sliver of light to come through from between the edge of the wall and the edge of the blind.
x | x | x |  | x |  |  |  | 2009-05-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Technical Clarification | 13 | In addition to the Credit Criteria stated in the technical manual, the following additional credit criteria have been developed. Projects using the following criteria can claim one point for this credit. This criteria can be used in conjunction to the criteria stated in the technical manual, or by itself. One point is awarded where it is demonstrated that glare from daylight is reduced through the fitting of blinds or screens on all glazing and atriums as a base building provision and meet the following criteria: - Eliminate 95% of all direct sun penetration - Have a visual light transmittance (VLT) of ≤10% - Can be controlled by all affected occupants within each floor or area. Projects seeking to claim this alternative methodology must use the compliance requirements and documentation guidelines for Occupant Controlled, Automated Blinds/Screens as stated in the credit criteria, with the exception of the provision of an automated motorized control for these blinds. For more information, please refer to clarification IEQ-4/12 (Office Interiors), IEQ-5/12 (Office), IEQ-11(All other tools)
x | [7 empty] | 2009-02-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Withdrawn | 14 | This Clarification was originally posted on February 2009. It has been replaced with Correction No. 18 Measurement of the vertical and horizontal displacement of the monitor arm must be at least 50cm total. Therefore, the required range of movement is 50cm vertically from the highest point to the lowest point and 50cm horizontally from either horizontal extremity, measured from the centre point of where the monitor arm is designed to attach to the monitor. Measurement can be done without a monitor attached.
x | x | x |  | x | x |  |  | 2009-03-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | CIR Ruling | 15 | The Credit Interpretation Request (CIR) to use Lux sensor modeling to demonstrate compliance with IEQ-5 is granted conditionally on the project’s ability to also provide modeling images of shadowing on the work plane for key times (namely at the start and end of each main block of un-shaded hours) which provide visual feedback of the shading performance. Note: Although the modeling approach using Lux sensors to determine when the shading system protects from direct sunlight is an acceptable method to determine the percentage of shading hours, it does not provide graphical confirmation of the shading performance.
x | x | x | [5 empty] | 2009-03-01 | IEQ-4 | IEQ-5 | IEQ-5 |  | Daylight Glare Control | Technical Clarification | 16 | A Green Star - Office Interiors project occupying a building that has achieved a Green Star - As Built rating that was awarded full points for IEQ-5 'Daylight Glare Control' is automatically awarded the first point for this credit provided that no modifications to the shading devices have occurred from the time of rating. Project's claiming this Deemed to Satisfy methodology must submit the following on their cover sheet: - The Design/As Built project name and number and the number of points achieved for this Credit; - State that the submission is relying on the base building project's shading systems; and - Stating that the building has not been modified from the time of rating.
|  | x | [5 empty] | 2009-03-01 |  | IEQ-5 |  |  | Daylight Glare Control | CIR Ruling | 17 | The Credit Interpretation Request (CIR) to prove compliance using the weighted average method as detailed in the Office Design v2 Technical Manual is denied.
x | [7 empty] | 2009-10-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Correction | 18 | The Additional Guidance for this credit now states that: Adjustable Arms Adjustable arms must have at least two articulations and be able to provide the monitor with a vertical and horizontal displacement, and be possitioned at any point within this displacement, as follows: • The horizontal displacement must be at least 50cm total measured from either horizontal extremity measured from the centre point of where the monitor arm is designed to attach to the monitor; and • The vertical displacement must be at least 18cm total measured as though there is a 19" monitor arm attached. Therefore, there must be at least a 10cm clearance between the surface of the table/desk and the center of the monitor arm. The displacement itself is then measured upwards from the center of the arm.
x | [7 empty] | 2009-10-01 | IEQ-4 | IEQ-5 | IEQ-5 |  | Daylight Glare Control | Technical Clarification | 19 | A Green Star - Office Interiors project occupying a building that meets the criteria for fixed shading devices from 'Daylight Glare Control' as stated in Green Star - Office v2 Design or Green Star - Office As Built v2 can claim the first point for this credit. To do so, the project must demonstrate that, for each typical glazing configuration for the space that the tenancy is occupying, fixed shading devices shade the working plane 1.5m in from the centre of the glazing, from 80% of direct sun. Project's claiming this methodology must submit the following: - A stereoraphic diagram at the working plane, 1.5m in from centre of that glazing system, demonstrating that the point is shaded for 80% of standard working hours; and - Drawings demonstrating the extent of fixed shading for each typical glazing system. For information on how to demonstrate compliance for this credit, see the applicable Green Star - Office Design v2 or Green Star - Office As Built v2 Technical Manual. Where the building that is being occupied has previously received a Green Star - As Built rating, and has achieved the point for fixed shading for this credit, please see Technical Clarification No.16
[6 empty] | x |  | 2013-11-01 |  |  |  | IEQ-11 | Daylight Glare Control | Correction | 20 | The following statement, found within the Compliance Requirements of the credit: The nominated plane must be shown to be shaded from direct sun for 80% of the nominated hours for the winter and spring equinox as well as the summer and winter solstices. Is being corrected to read: The nominated plane must be shown to be shaded from direct sun for 80% of the nominated hours for the spring and autumn equinox as well as the summer and winter solstices.
|  | x |  | x |  |  |  | 2009-03-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Documentation (Design) | A | Where the Credit Criteria is being met entirely through blinds/screens, projects can substitute Tender Façade Drawings with Tender Plan Drawings provided that all information required by the Technical Manual has been included.
[8 empty] | 2009-03-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Documentation (As Built) | B | Where the Credit Criteria is being met entirely through blinds/screens, projects can substitute As Built Façade Drawings with As Built Plan Drawings provided that all information required by the Technical Manual has been included.
|  | x |  | x |  |  |  | 2011-01-01 | IEQ-4 | IEQ-5 | IEQ-5 | IEQ-11 | Daylight Glare Control | Documentation (As Built) | C | This clarification was originally posted in March 2009. It has been amended to remove reference to glazing. Documentation for As-Built Rating for this credit, no longer requires the following: • Confirmation from suppliers; • Confirmation from sub-contractors. Additional documentation required for As-Built rating for this credit is as follows: • Confirmation from the head contractor that all glare control devices were installed as per the As-Built drawings submitted; • Confirmation from the head contractor that all types of glare control devices correspond with the Manufacturer's Data Sheets submitted.
x | x | x |  | x | x | x |  |  | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts
x | x | [6 empty] | 2007-12-01 | IEQ-5 | IEQ-6 |  |  | High Frequency Ballasts | Technical Clarification | 1 | When referencing ballasts, the term ‘electronic’ is considered synonymous with ‘high frequency’.
x | x | x |  | x | x | x |  | 2008-12-01 | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts | Technical Clarification | 2 | When all the lighting in the relevant area of the project (as stated in the Credit) is fluorescent lighting with high frequency ballasts installed, the project team is not required to provide a summary sheet. In its place, unless the specifications clearly state that “all” items must comply, project teams can provide a letter from the relevant consultant confirming that this is the case or clearly state through the drawings that these meet the criteria.
x | x | x |  | x | x | x |  | 2009-04-01 | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts | Technical Clarification | 3 | Where only T5 lamps have been specified/installed, this credit is automatically awarded. Confirmation from the electrical or lighting engineer stating that all lamps meet this criteria must be provided at the time of submission. No other documentation is required.
|  | x |  | x | x | x |  | 2009-03-01 | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts | Documentation (Design) | A | Projects can substitute Extract(s) from the specification(s) with Luminaire Schedule provided that the schedule clearly shows that high frequency ballasts are being used for all luminaires listed.
|  | x |  | x | x | x |  | 2009-03-01 | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the supplier(s) * Confirmation from the Contractor
x | x | x |  | x | x |  |  | 2013-11-01 | IEQ-5 | IEQ-6 | IEQ-6 | IEQ-12 | High Frequency Ballasts | Documentation | C | Based on feedback from assessors and project teams, the following documentation is no longer required: Design rating: - Short report - Extract(s) from the specification(s) As Built rating: - Short report - As-built drawings - Confirmation from the supplier(s) - Confirmation from the contractor Projects must submit the following documentation instead: - A letter from the project's GSAP confirming compliance with the Credit Criteria.
x | x | x |  | x | x | x | x |  | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels
x | x | [6 empty] | 2011-01-01 | IEQ-6 | IEQ-7 |  |  | Electric Lighting Levels | withdrawn | 1 | This clarification has been withdrawn. See Technical Clarification No. 11 for more information. (Originally posted on Dec-07) The aim of this credit is to encourage and reward moderation in office lighting levels. Therefore calculations for this credit must be based on the maximum illuminance levels available in each area. Any reduction in lighting levels, caused by commissioning or dimming must be disregarded. This is necessary because tenants can alter commissioning and dimming.
x | x | [6 empty] | 2006-01-01 | IEQ-6 | IEQ-7 |  |  | Electric Lighting Levels | Technical Clarification | 2 | The Credit Criteria stipulates the maximum (at any point), not average (over a floor or space) value for maintained illuminance. Maintained illuminance refers to the average illuminance of a light fitting over its life time (dust and other factors taken into account). In order to claim the credit, the maintained illuminance values must not exceed 400 Lux for 95% of the NLA. (Amended to change wording from luminance to illuminance)
|  | x |  | x | x |  | x | 2006-01-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Technical Clarification | 3 | Where the values for the surface reflectance are unknown, the values for modelling these credits must be in accordance with the values stated in the Compliance Requirements section of IEQ-4 'Daylight'.
x | [7 empty] | 2008-01-01 | IEQ-6 |  |  |  | Electric Lighting Levels | Withdrawn | 4 | This clarification has been withdrawn. See Technical Clarification No. 11 for more information. (Originally posted on Jan-08) The Credit Interpretation Request (CIR) to use dimmers combined with lumen sensors as an alternative, but equivalent strategy for meeting the Aim of the Credit is denied. The energy benefits of the proposed solution are picked up in the Energy Category; this credit is specifically intended to avoid over-design of lighting systems.
x | [7 empty] | 2008-01-01 | IEQ-6 |  |  |  | Electric Lighting Levels | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to meet the Credit Criteria through a suspended overhead task lighting system that illuminates up to two workstations at a time is granted conditionally on the project’s ability to clearly demonstrate the following: 1. The suspended overhead task lighting is connected to both workstations for individual control; 2. The overhead task lighting must be connected to the tenants’ light control system; 3. The Lux levels specified in the Credit Criteria must be met for the specified NLA; and 4. The system installed and any assumptions made are reflected throughout the rest of the design and submission (e.g. in submissions for Ene-1, Ene-2, Ene-4, IEQ-5, etc.).
x | x | x |  | x |  |  |  | 2008-03-01 | IEQ-6 | IEQ-6 | IEQ-6 |  | Electric Lighting Levels | CIR Ruling | 6 | The CIR to exempt the “video-conferencing mode” settings for a video-conferencing room from meeting the criteria of this credit is granted conditionally on the project’s ability to demonstrate that the video-conferencing room is in fact equipped for videoconferencing, that the default setting of the room is less than 400 Lux, and that the lighting controls will automatically reset the room’s illumination levels back to the default level when the video-conferencing equipment is not in operation.
x | x | x | [5 empty] | 2009-02-01 |  | IEQ-6 | IEQ-6 |  | Electric Lighting Levels | Technical Clarification | 7 | In addition to the working plane levels stated in the credit criteria, projects can show the required lux levels at a working plane of 700mm AFFL as per AS1680.1-2006.
x | x | [6 empty] | 2009-05-01 | IEQ-6 | IEQ-7 |  |  | Electric Lighting Levels | Technical Clarification | 8 | Originally posted on Jan-06 Where the values for the surface reflectance are unknown, the values for modelling these credits must be in accordance with the values stated in AS 1680.1 Interior Lighting - General Principles and Recommendations as per the IEQ-3 Daylight credit (Office Interiors) or IEQ-4 'Daylight' (Office). Otherwise the actual reflectance values should be used, as stated in the Technical Manual.
|  |  |  | x |  |  |  | 2009-07-01 |  |  |  | IEQ-13 | Electric Lighting Levels | Technical Clarification | 9 | As per AS1680.2.3 clause E2 (a), “if a particular interior/activity is not specifically listed in Column 1 (of Table E1), the recommendations for a comparable interior/activity should be adopted, as appropriate.” Therefore, exhibition spaces should adopt the ‘Assembly hall – General use’ criteria set out in Table E1.
|  |  |  | x |  |  |  | 2009-07-01 |  |  |  | IEQ-13 | Electric Lighting Levels | Technical Clarification | 10 | With regards to spaces with multiple uses (e.g. lobby which can also double as an exhibition space), a project may have multiple light controls according to the different uses of the space. However, for the purposes of Green Star, such project must demonstrate how the Primary use of the space (e.g. lobby) complies with the Credit Criteria. Additionally, the project must demonstrate that the space is equipped for a secondary use (e.g. exhibition space), and that the primary use setting of the room is the required level for the room. Furthermore, it must be shown that the lighting controls will automatically reset the room’s illumination levels back to the primary use level when the secondary use mode is not in operation.
x | x | x |  | x | x | x | x | 2009-10-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | CIR Ruling | 11 | A dimmable lighting system can be used as an alternative method of compliance for this credit. The project team must demonstrate that: • The system has been configured to be at a maintained illuminance level as per the Credit Criteria; • The lighting control system has 'restricted' occupant control i.e. A user cannot change the settings to increase the lux levels above the requirements of the Technical Manual; • Where sensors are used to monitor light levels, the lights controlled by it must be within the ‘field of view’ of the sensor (i.e. if a sensor has a 4m radius, then the centre of each controlled light must be within this zone); • The Building Guides include a specific section detailing how and when occupants can control the light levels and how dimming can change the colour of the lamp (ie a purple fluorescent tube is a sign of extensive dimming, not that the light isn’t working); and • Commissioning has been (or will be in the case of a design rating) undertaken to show that light levels have been set for each light fitting via measurement, and that , if any, the sensors have not been overridden, Please note that when assessing lighting energy consumption, the projects must either allow for full power (ie no dimming) or provide evidence of the light’s power consumption at various dimming levels.
|  |  |  | x |  |  |  | 2009-10-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Technical Clarification | 12 | The table referred to in the credit criteria is Table E1 of AS1680.2.3-1994. Project teams may also use Table D1 of AS/NZS1680.2.3-2008.
x | x | x |  | x | x | x | x | 2011-01-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Correction |  | Where reflectance values are known, they must be used in modelling for this credit in accordance with the requirements in the Technical Manual. For a Green Star - Design submission where surface reflectance values are unknown; reflectance values used for the IEQ-3 Daylight credit (Office Interiors) or IEQ-4 'Daylight' (Office) must be used; where the Daylight credit isn't claimed the surface reflectance values listed below should be used. The following Reference Values can be used where values are unknown in a Green Star - Design rating: - 0.2 for floors (assumes a light coloured carpet) - 0.5 for walls (assumes white paint) - 0.7 for ceilings (assumes white paint) - 0.3 for internal partitions - 0.2 for ground. For Green Star As built submissions the actual surface reflectance values must be used.
|  |  |  | x |  |  |  | 2012-08-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Technical Clarification | 14 | A combination of measurements and modelling may be used to demonstrate compliance with the credit criteria. If this approach is adopted then the project submission must include: Marked-up schematics showing the areas which demonstrate compliance through measurement and the areas which demonstrate compliance by design implementation; For the areas which have been nominated to demonstrate compliance by measurement, all documents required by the technical manual for that approach. For the areas which have been nominated to demonstrate compliance by design implementation, all documents required by the technical manual for that approach.
|  | x |  | x |  |  |  | 2009-03-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extracts from the specifications * Isometric lighting measurement drawings Projects must submit the following documentation instead: * Isolux Plot Drawings marked up to show the location and size of all areas where maintained illuminance levels exceed 400 lux, and correlated with the short report. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x |  | x |  |  |  | 2009-03-01 | IEQ-6 | IEQ-7 | IEQ-7 | IEQ-13 | Electric Lighting Levels | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Isometric as-built floor plan drawings Projects must submit the following documentation instead: * As Built Isolux Plot Drawings marked up to show the location and size of all areas where maintained illuminance levels exceed 400 lux. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x |  | x | x | x | x |  | IEQ-7 | IEQ-8 | IEQ-8 | IEQ-14 | External Views
x | x | [6 empty] | 2007-12-01 | IEQ-7 | IEQ-8 |  |  | External Views | Technical Clarification | 1 | 1. If the office space opens directly to the atrium (i.e., no internal glazing is installed), then the internal perimeter of the atrium may be used for the calculations. 2. The base of the internal atrium is considered to be at the lowest level of Class 5 Commercial Office space (even if the actual base of atrium is several floors lower). 3. The minimum daylight factor of 3.5% is for any point within the atrium. 4. The minimum daylight factor can be demonstrated either at the base of the atrium (as per the Technical Manual), OR at the base of each level for which compliance with the Credit Criteria is claimed. 5. In 'Additional Guidance', "minimum 8m sight line across the atrium" can be no less than 45 degrees to the vision glazing or atrium edge. The atrium must be at least 8 meters wide at any point to which the line of sight is demonstrated.
| x | x |  | x | x | x | x | 2008-04-01 |  | IEQ-8 | IEQ-8 | IEQ-14 | External Views | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to confirm that a proportion of an atrium space with a minimum Daylight Factor (DF) of 3.5% which is immediately adjacent to the occupied space can be included when determining the area of external view for the credit is granted. Please note that the Certified Assessors will be looking for suitable evidence that shows that this proportion of the atrium space has a DF of 3.5%. Please see the Technical Manual for information on what the project must submit to comply with this credit. Furthermore, any remaining nominated area adjacent to the areas of the atrium that does not have a DF of 3.5% cannot contribute to achieving this credit.
| x | x |  | x | x |  | x | 2008-07-01 |  | IEQ-8 | IEQ-9 | IEQ-14 | External Views | Technical Clarification | 3 | The distance to the nearest vision glazing is to be no more than 8 meters. The view must extend from any claimed indoor area for 8m; e.g. in order to claim area at the perimeter of the building, there must not be solid structures blocking the view for 8m from the building.
x | [7 empty] | 2007-12-01 | IEQ-7 |  |  |  | External Views | Technical Clarification | 4 | As the Credit Criteria is based on 'work settings', not 'NLA', please note the following typos: Within the second bullet point under Compliance Requirements, 'NLA' should read 'work settings', as follows: "Calculations that show the work settings that are within eight metres of vision glazing as a fraction of the total work settings." In the last paragraph in Compliance Requirements, 'NLA' should also read 'work settings', as follows: "The Assessor(s) will not award points unless it is demonstrated that the required work settings are within eight meters..." 1. If the office space opens directly to the atrium (i.e., no internal glazing in installed), then the internal perimeter of the atrium may be used for the calculations. 2. The base of the internal atrium is considered to be at the lowest level of Class 5 Commercial Office space (even if the actual base of atrium is several floors lower).
x | [7 empty] | 2007-12-01 | IEQ-7 |  |  |  | External Views | Technical Clarification | 4 | 3. The minimum daylight factor of 3.5% can be demonstrated either at the base of the atrium (as per the Technical Manual), OR at the base of each level for which compliance with the Credit Criteria is claimed. 4. In 'Additional Guidance', "minimum 8m sight line across the atrium" can be no less than 45 degrees to the vision glazing or atrium edge. The atrium must be at least 8 meters wide at any point to which the line of sight is demonstrated.
x | [7 empty] | 2009-07-01 | IEQ-7 |  |  |  | External Views | Technical Clarification | 5 | The distance to the nearest vision glazing is to be no more than 8 meters. The view must extend from any claimed indoor area for 8m; e.g. in order to claim area at the perimeter of the building, there must not be solid structures blocking the view for 8m from the building.
x | x | x |  | x | x | x | x | 2009-10-01 | IEQ-7 | IEQ-8 | IEQ-8 | IEQ-14 | External Views | Correction | 6 | The following guidance applies to projects relying on atria to achieve compliance with this credit: Where compliance is achieved through a day-lit atrium, the following must be achieved: The atrium must be at least eight metres wide at any point to which the line of sight is demonstrated. • If the space opens directly onto the atrium, calculation must be made from the vision glazing or from the internal perimeter of the atrium if no internal glazing is installed; • The area behind any solid portion of the atrium perimeter must be excluded from the calculations; and • The minimum daylight factor of 2.5% (done in accordance with IEQ-4) is for 90% of the atrium area at the bottom of the atrium.
| x | x | x | x | x | x | x |  |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort
| x | [6 empty] | 2007-12-01 |  | IEQ-9 | IEQ-9 |  | Thermal Comfort | Technical Clarification | 1 | The Credit Criteria applies to Class 5 Commercial Office NLA only.
| x | x | x | x | x |  | x | 2007-08-01 |  | IEQ-9 |  | IEQ-5 | Thermal Comfort | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to use an approximation of the estimated thermal and visual properties of an existing façade (e.g., the U-values and shading coefficients of walls/glazing) is granted conditionally on the ability of the submission to justify that at all times, the assumptions have been conservative, i.e. described the ‘worst case scenario’. Should any project seek confirmation whether its assumptions are sufficiently conservative, CIRs justifying the assumptions must be submitted.
| x | x | [5 empty] | 2008-07-01 |  | IEQ-9 | IEQ-9 |  | Thermal Comfort | Technical Clarification | 3 | Under Additional Guidance - Zone Distribution, the Technical Manual states that “Perimeter zones of less than four metres shall be modelled independently to prevent averaging of heat fluxes and temperatures from invalidating the results (i.e. the comfort predictions shall be measured two metres from the internal face of the façade).” As the meaning of the quoted sentence is unclear, the following wording is provided to replace and clarify the first sentence: - Zoning shall match the air conditioning zones; - For equitable assessment, perimeter zones shall have a depth of 4 meters; - Each perimeter shall be reported independently (e.g. North, South, East and West); - Perimeter zones shall be reported independently of interior zones; - Model shall be completed with all systems assessed simultaneously; and - Comfort predictions shall be measured at the mid point of each zone, i.e. if the perimeter zone is 3.6m deep then the comfort prediction will be 1.8 from the perimeter; OR Comfort predictions shall be taken as an average across the zone.
| x | x |  |  |  |  | x | 2008-12-01 |  | IEQ-9 | IEQ-9 |  | Thermal Comfort | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to deem IEQ-9 ‘Thermal Comfort Modeling’ Not Applicable (NA), as the project is being delivered as a shell and core project, is denied. This Credit is applicable regardless of how the project is delivered. Making this Credit ‘NA’ would require a change in benchmarks to this Credit. The project team must make all the necessary assumptions about the systems to indicate compliance with the Credit. In this way shell and core delivery does not impede assessment of the development.
| x | x | x | x | x |  | x | 2008-12-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 5 | As-Built projects that have been previously awarded points for these credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credit (i.e. same shape floor plan, same glazing propoerties and floor-to-ceiling height) can submit a letter from the relevant consultant in place of an as-built model (the as-built drawings must still be provided). The letter must describe the extent of any changes and state the maximum impact they may have on the building performance if it were remodelled. In this case the number of points achieved in the Design rating will automatically be awarded. Please note: Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Modelling must account for worse case scenario; please see the assumptions clarification for more information.
| x | x | x | x | x | x | x | 2008-12-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 6 | To ensure consistency across the documentation provided within Green Star, projects do not need to submit the “Supplier Certification for all glazing showing the type, quantity and data sheets for each type of glass supplied” required in the Technical Manual. The documentation requirements for this Credit have been revised as follows: - A thermal comfort report demonstrating how the finished building complies with the Criteria of the Credit and reference where appropriate the additional documentation. The report must contain: - The thermal modelling simulation output including hourly PMV levels for each day of the year that the space is occupied; - A summary of radiant temperatures, air temperatures and humidity from the simulation; and - Details of the weather data used. - Copies of as-built plan drawings clearly showing each zone assessed for thermal comfort; - Copies of as-built façade and roof drawings and elevations to show the façade materials in the design, including the type of glass supplied; - Supplier or Manufacturer Data Sheets for each supplied glass; - Commissioning reports demonstrating correct operation of the mechanical ventilation or natural ventilation system.
|  |  |  | x |  |  |  | 2009-07-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Withdrawn | 7 | See correction No.12 (Originally Posted March 2009) The credit criteria for this credit has been modified. It now reads: Up to three points are awarded where the following is demonstrated: Naturally Ventilated and Mechanically Assisted Naturally Ventilated Spaces * One point is awarded where individual user control of ventilation openings no less than 0.75m2 is provided for every four (or fewer) workstations. * Two additional points are awarded where the Acceptability Limits of ASHRAE Standard 55‑2004 are achieved during Standard Operating Hours of Occupancy for 98% of the year: - One point for internal temperatures within 80% of Acceptability Limit 1; and - Two points for internal temperatures within 90% of Acceptability Limit 1.
|  |  |  | x |  |  |  | 2009-07-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Withdrawn | 7 | Mechanically Air‑Conditioned Spaces * Two points are awarded where Predicted Mean Vote (PMV) levels, calculated in accordance with ISO7730, are achieved during Standard Operating Hours of Occupancy for 98% of the year using standard clothing and metabolic rate values: - One point for PMV levels between ‑1 and +1, inclusive; and - Two points for PMV levels are between ‑0.5 and +0.5, inclusive. * One additional point is awarded where either one or two points are achieved above and control of air supply rates, air temperature, or radiant temperature is provided for every four (or fewer) workstations. Mixed mode Ventilated Spaces For mixed mode buildings, the above mechanical and natural ventilation thermal comfort criteria must be met. For the purposes of this credit ‘nominated area’ is UFA, excluding external covered areas. The point for individual thermal comfort control need not be assessed for libraries, canteens or gymnasiums (as defined in the Energy Calculator Guide).
| x | x | x | x | x |  | x | 2009-05-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 8 | For Naturally Ventilated Buildings only: For areas where the mean outdoor monthly temperature is less than the low temperature limit of 10C as stated within ASHRAE Standard 55, projects can meet the requirements of this credit by ensuring that the minimum indoor temperatures is kept at the minimum limit stated within the standard. For example, if the mean outdoor monthly temperature is 9C the project can meet the standard by ensuring that the comfort conditions in the building remain between the range of 18C and 24C as per Figure 5.3 found within ASHRAE Standard 55. Please note: Extrapolating the temperatures is not allowed. Projects cannot claim that the criteria for this credit has been met by providing indoor temperatures lower than those within the standard.
|  |  |  | x |  |  |  | 2009-05-01 |  |  |  | IEQ-5 | Thermal Comfort | Technical Clarification | 9 | The additional point in the credit relevant to workstations for Mechanically Air-conditioned Spaces and for Mixed mode Ventilated Spaces is intended to be applicable to areas that contain a workstation. A workstation is defined as a desk and a chair where a person works. Where the space contains a table where more than one person will regularly sit (such as a lab, or a classroom with larger tables), up to two chairs on a desk are equivalent to one workstation. Office areas, meeting rooms, classrooms and laboratories are typical areas that would contain workstations.
|  |  |  | x |  |  |  | 2009-05-01 |  |  |  | IEQ-5 | Thermal Comfort | Technical Clarification | 10 | PMV thermal comfort calculations are useful even in spaces such as auditoriums. Where a space, such as a welding area, is required to have conditions which would exceed the requirements for good thermal comfort, the project must submit a CIR explaining their arguments for excluding this space.
|  |  | x |  |  |  |  | 2009-05-01 |  |  |  | IEQ-5 | Thermal Comfort | Correction | 11 | This correction applies to all projects registered after this date. Projects registered prior may choose to follow the Technical Manual or this Clarification. The following Credit Criteria is being modified from: Where the Acceptability Limits of ASHRAE Standard 55-2004 are achieved during Standard Operating Hours of Occupancy for 98% of the year: - One point is awarded for internal temperatures within 70% of Acceptability Limit 1 To: Where the Acceptability Limits of ASHRAE Standard 55-2004 are achieved during Standard Operating Hours of Occupancy for 98% of the year: - One point is awarded for internal temperatures within 80% of Acceptability Limit 1 Any reference in the Technical Manual to 70% of Acceptability Limit 1 should now read 80% of Acceptability Limit 1.
|  |  |  | x |  |  |  | 2009-07-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Correction | 12 | The Credit Criteria for this credit has been modified. It now reads: Up to three points are awarded where the following is demonstrated: Naturally Ventilated and Mechanically Assisted Naturally Ventilated Spaces * Two points are awarded where the Acceptability Limits of ASHRAE Standard 55‑2004 are achieved during Standard Operating Hours of Occupancy for 98% of the year: - One point for internal temperatures within 80% of Acceptability Limit 1; and - Two points for internal temperatures within 90% of Acceptability Limit 1. * One additional point is awarded where individual user control of ventilation openings no less than 0.75m2 is provided for every four (or fewer) workstations.
|  |  |  | x |  |  |  | 2009-07-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Correction | 12 | Mechanically Air‑Conditioned Spaces * Two points are awarded where Predicted Mean Vote (PMV) levels, calculated in accordance with ISO7730, are achieved during Standard Operating Hours of Occupancy for 98% of the year using standard clothing and metabolic rate values: - One point for PMV levels between ‑1 and +1, inclusive; and - Two points for PMV levels are between ‑0.5 and +0.5, inclusive. * One additional point is awarded where either one or two points are achieved above and control of air supply rates, air temperature, or radiant temperature is provided for every four (or fewer) workstations. Mixed mode Ventilated Spaces For mixed mode buildings, the above mechanical and natural ventilation thermal comfort criteria must be met. For the purposes of this credit ‘nominated area’ is UFA, excluding external covered areas. The point for individual thermal comfort control need not be assessed for libraries, canteens or gymnasiums (as defined in the Energy Calculator Guide).
[7 empty] | x | 2009-07-01 |  |  |  | IEQ-5 | Thermal Comfort | Technical Clarification | 13 | Ceiling fans must be provided, as a minimum, in the living room and in all available bedrooms in order to claim the first point of this credit.
|  |  |  | x |  |  |  | 2011-01-01 |  |  |  | IEQ-5 | Thermal Comfort | Correction | 14 | Thermal comfort calculations must use the hours of operation specified in the 'Green Star - Education v1 Energy Calculator Guide' . 'HVAC Model Operational Profiles' are defined for different space types in the guide. Space types are defined in the guide.
| x | x | x | x | x | x |  | 2011-01-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 15 | Spaces with ceiling fans can be assessed under the criteria for Mechanically Air-conditioned spaces. PMV modelling is an acceptable method for showing compliance for these areas.
[7 empty] | x | 2011-01-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 16 | The Credit Criteria states "Two points are awarded where average heating and cooling loads of less than 30MJ/m2 are achieved". In other words the average heating plus the average cooling loads must be less than 30MJ/m2.
|  | x |  | x | x | x |  | 2012-08-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 17 | ASHRAE standard 55-2010 can be used in place of the ASHRAE Standard 55-2004 which is referenced by the credit.
|  | x |  | x | x | x | x | 2012-08-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Technical Clarification | 18 | For Design projects where thermal properties of constructions have not yet been specified, project teams may assume NCC Deemed-to-satisfy thermal performance. In these situations the project team may replace "extract(s) from the specification(s)" with the following documentation to demonstrate the thermal properties of new material constructions used in the model: A section within the Modeling Report which lists all material types which form the building envelope and nominates whether: 1. The material constructions and properties have been specified (in which case a specification will still be required for these materiasl); or 2. The NCC deemed-to-satisfy performance has been assumed. - Where material constructions and properties have been specified and shown on drawings, the project team must provide calculations to demonstrate the thermal properties of the constructions using industry standard values; - Where the NCC deemed-to-satisfy performance has been assumed, the specification must require adherence to the deem-to-satisfy requirements of NCC Section J for the year in which the project obtained DA approval. The project team must also demonstrate that the thermal properties used are consistent across all other modelling credits within the submission.
|  |  | x |  |  |  |  | 2013-11-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Correction | 20 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
| X | X | X | X | X |  |  | 2013-11-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Correction | 21 | Additional Guidance in the IEQ Thermal Comfort credit state that: "Any shading that meets the Credit Criteria of IEQ-5 ‘Daylight Glare Control’ can be included in thermal modelling estimations; all other shading and blinds must be excluded." This wording is corrected to: "All fixed external shading must be included in thermal comfort modelling. There is no need to demonstrate compliance with the Daylight Glare Control credit for these shades to be included in Thermal Comfort modelling. Internal blinds must meet the requirements of IEQ-5 'Daylight Glare Control' to be included in Thermal Comfort modelling."
| X | X | x | x | x | x |  | 2013-11-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | CIR Ruling | 22 | Deemed-to-satisfy (DTS) requirement for fully mechanically air conditioned buildings. The following is a deemed to satisfy approach to demonstrating PMV values of between +1 and -1. Thermal modelling is still required to demonstrate PMV values of between +0.5 and -0.5. HVAC requirements: 1. Dry Bulb Temperature in space is controlled to 20°C to 24°C; 2. The HVAC system has separate internal and perimeter zones with independent temperature control which meet the following maximum zone size requirements: 85m2 perimeter zone, 120m2 internal zone for 95% of NLA. 3. Each HVAC zone contains its own temperature sensor(s). Facade requirements: 1. This DTS ruling cannot be applied to a refurbishment project that reuses any portion of existing facade. It can only be used if the entire building fabric is new. Please contact the GBCA if you would like to use a modified version of this ruling for a refurbishment project. Documentation requirements At the time of a Green Star - Design submission, please provide the following: • Short report summarising how each of the above criteria have been met, referencing supporting information. • Extracts from the mechanical specifications showing the clauses demonstrating the above mechanical criteria have been met • Marked up Tender Mechanical Drawings demonstrating mechanical zoning criteria listed above have been met. No further documentation is required. At the time of a Green Star - As Built submission, please provide the following: • Short report summarising how each of the above criteria have been met, referencing supporting information. • Confirmation from the relevant sub-contractors that all services have been installed and commissioned in line with the above listed criteria • Marked up As-Built Mechanical Drawings demonstrating mechanical zoning criteria listed above have been met. No further documentation is required.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Extract(s) from the specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x | 2013-11-01 |  | IEQ-9 | IEQ-9 | IEQ-5 | Thermal Comfort | Documentation | B | Where one point is being claimed for providing ceiling fans for at least 95% of all apartments, please submit the following evidence and ensure it readily confirms compliance: Design rating: - Short Report prepared by a suitable professional that describes how the Credit Criteria has been met by including a calculation indicating the number of apartments with ceiling fans specified as a percentage of the total number apartments; - Tender Drawings clearly marked up indicating the location of ceilings fans to be installed within the specified apartments. As Built rating: - Short Report prepared by a suitable professional that describes how the Credit Criteria has been met by including a calculation indicating the number of apartments with ceiling fans installed as a percentage of the total number apartments; - As Built Drawings clearly marked up indicating the location of ceilings fans that have been installed within the specified apartments. Where 2 points are being claimed, all documentation as per the Technical Manual must be submitted for assessment.
x | x | x |  |  | x | x |  |  | IEQ-8 | IEQ-10 | IEQ-10 | IEQ-15 | Individual Thermal Comfort Control
x | x | [6 empty] | 2008-12-01 | IEQ-10 | IEQ-10 |  |  | Individual Thermal Comfort Control | Technical Clarification | 1 | For naturally ventilated spaces, operable windows (with an operable area of not less than 0.75m2), are awarded as follows: - One point where openings are provided for every 30m2 of the NLA; and - Two points where openings are provided for every 15m2 of the NLA.
|  | x | [5 empty] | 2009-05-01 | IEQ-8 | IEQ-10 | IEQ-10 | IEQ-15 | Individual Comfort Control | Technical Clarification | 2 | This credit is intended to reward the physical provision of individual comfort control to the building occupants. This makes documentation of a provision that the HVAC ducting is arranged in a manner which may allow for the tenant to install specialised workstations to actually deliver the individually controlled air flow unacceptable. The provision of both the ducting arrangement and the actual workstations to long-term building occupants as a base building integrated fitout initiative is an example of a design and contractual solution that would satisfy the intent of the credit but they must be documented and delivered together.
x | [7 empty] | 2011-01-01 | IEQ-8 |  |  |  | Individual Thermal Comfort Control | Technical Clarification | 3 | The ‘Additional Point’ is ‘Not Applicable’ when zero points are awarded in the Credit Criteria.
|  | x |  |  | x | x |  | 2009-03-01 | IEQ-8 | IEQ-10 | IEQ-10 | IEQ-15 | Individual Thermal Comfort Control | Documentation (Design) | A | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is naturally ventilated and meets the requirements of IEQ-1 'Ventilation Rates', the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: For Naturally Ventilated Spaces: * Schedule of ventilation openings -OR- Empirical calculations -OR- Computer modelling report Furthermore, the following documentation is being modified: * Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Describing how the design provides for individual control, detailing its operation, accessibility and controls; - Providing a summary table of the naturally ventilated, mixed mode ventilated, mechanically air conditioned or MANV spaces in the building, their areas, the AHU(s) or ventilation openings that serve each space; and - Referencing the tender drawings and the extract(s) from the specification(s). All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x |  |  | x | x |  | 2009-03-01 | IEQ-8 | IEQ-10 | IEQ-10 | IEQ-15 | Individual Thermal Comfort Control | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit, provided that no automation controlling the flow of natural ventilation, such as automated louvres, has been provided: For Naturally Ventilated Spaces: * Extract(s) from the Commissioning Report Furthermore, the Extract(s) from the Commissioning Report required for mechanically air conditioned spaces, must show that the system, as installed, works as intended and can be operated by the user. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x |  | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos
| x | [6 empty] | 2006-01-01 |  | IEQ -11 |  |  | Hazardous Materials / Asbestos | Technical Clarification | 1 | For Green Star - Office Design (not Green Star - Office As Built), a contractual commitment to remove asbestos (according with the stipulations of the Technical Manual) meets the Credit Criteria, as does evidence that asbestos has been removed.
x | x | x | x | x |  |  |  | 2008-03-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Technical Clarification | 2 | Since use of asbestos has been banned in Australia, this credit is automatically deemed ‘Not Applicable’ for any new building on a non-contaminated greenfield site that began construction in 2005 or later. This does not apply to any project where any demolition of existing building(s) occurs, and the Credit Criteria must be met.
x | [7 empty] | 2008-03-01 | IEQ-9 |  |  |  | Hazardous Materials / Asbestos | Technical Clarification | 3 | Any area that is accessed or uncovered by contractors as part of fitout works that might contain asbestos must form part of the survey and removal, if applicable. This can include areas such as risers of plant rooms if works are carried out in those areas. Ceiling voids must be included within the asbestos survey and removal. Since use of asbestos has been banned in Australia, this credit is automatically deemed ‘Not Applicable’ for any fitout in a new building which was begun on a non-contaminated greenfield site that begun construction in 2005 or later.
x | x | x | x | x | x |  | x | 2009-04-01 | IEQ-10 | IEQ-12 | IEQ-11 | IEQ-6 | Hazardous Materials | Technical Clarification | 4 | A new development is defined as a development on a site with no existing buildings at the time of purchase
x | x | x | x | x | x |  | x | 2011-01-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Correction | 5 | In order to claim this credit as 'not applicable', the following documentation must be submitted for Green Star certification: -For existing buildings where no Asbestos, Lead or PCBs have been found, a hazardous materials survey must be provided. -For new building developments, a credit cover sheet must be provided. A statement must be clearly written on the cover sheet, confirming that the building is a new development.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Technical Clarification | 6 | The asbestos survey must directly address the entire area of the fitout being assessed. Compliance cannot be demonstrated by assumptions based on survey results for other parts of the building.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Correction | 7 | Where all buildings on the site are demolished, this credit can be claimed as 'Not Applicable. The cover letter for this credit must state that all existing buildings were demolished. This confirmation must correlate with the information in the general section of the submission.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Documentation (Design) | A | Where the asbestos, lead or polychlorinated biphenyls were found, the following supplementary documentation can be provided instead of Hazardous materials survey: *Contractual commitment from the contractor (or suitable sub-contractor(s)) that the asbestos, lead and PCBs will be removed and disposed of in accordance with the standards listed under Compliance Requirements, or in the case of asbestos, the relevant environmental and OH&S legislation.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-10 | IEQ -11 | IEQ -11 | IEQ-6 | Hazardous Materials / Asbestos | Documentation (As Built) | B | Where the asbestos, lead or polychlorinated biphenyls were found, the following supplementary documentation can be provided instead of Disposal Receipts: * Hazardous materials survey where asbestos, lead or PCBs were found in the initial survey, a second survey must be conducted after the removal of the hazardous materials, confirming that no hazardous materials are present on the site.
x | [7 empty] | 2013-11-01 | IEQ-9 | IEQ -11 | IEQ -11 | IEQ-6 | Asbestos | Documentation (Design & As Built) | C | The credit is automatically recognised as being 'not applicable', where the fitout is located within a Green Star Office - Design or As Built certified building that was awarded 'not applicable'. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related certified project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
x | x | x | x | x | x | x | x |  | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels
| x | [6 empty] | 2006-01-01 |  | IEQ-12 |  |  | Internal Noise Levels | Technical Clarification | 1 | Credit Criteria refers to Design Sound Levels in Table 1 of AS/NZS 2107:2000. The reverberation times recommended by AS 2107:2000 are not required to be met to achieve the credit. Internal partitions need only be considered if they form part of the base building (e.g. structural walls of internal offices).
x | x | x | x | x | x | x | x | 2007-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem the mechanical engineer's contractual obligation to meet the Credit Criteria as alternative but equivalent compliance with the Aim of the Credit is denied as it poses an increased measure of uncertainty over the facility's attributes. Green Star assesses building attributes and rewards them for ensuring a superior environmental outcome - while in the areas of management, contractual relationships are a viable measure of outcome, in the areas of design they are not so - in part because subsequent design decisions will require client endorsement prior to implementation (due to cost implications).
| x | x | x | x | x |  | x | 2007-12-01 |  | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 3 | As acoustic reports are very frequently questioned in the Round 1 assessment, the GBCA offers the following advice to enhance their ability to communicate compliance: - The acoustic consultant must reach a conclusion that supports compliance with the Credit Criteria. - The data provided in the report should clearly justify the conclusion and account for all constant noise sources (hydraulic and mechanical systems that are both internal and external to the space, traffic, etc.). - In most cases, it is in the interest of the project to provide a tabulated summary listing the noise levels in all relevant spaces and comparing them to the values prescribed in the standard.
x | [7 empty] | 2007-12-01 | IEQ-10 |  |  |  | Internal Noise Levels | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to alter the band of reverberation times due to a non-standard workplace or to deem the credit 'Not Applicable' is denied because the warehouse will host office-related tasks (making it a standard workplace), and it is not clear why higher volume of space suggests that different criteria is acceptable.
x | [7 empty] | 2008-08-01 | IEQ-10 |  |  |  | Internal Noise Levels | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to undertake the complete acoustic testing in an occupied tenancy by having the space emptied during normal working hours on a work day is granted conditionally on the projects ability to demonstrate that: - The testing was done on a standard day; - The space was unoccupied during testing; - The space meets the Credit Criteria, Compliance Requirements and Additional Guidance stated in the Technical Manual; and - That testing specifically meets AS/NZS 2107:2000 compliance requirements. The acoustic engineer responsible for testing must clearly certify that these conditions were met.
| x | x | [5 empty] | 2008-12-01 |  | IEQ-12 | IEQ-12 |  | Internal Noise Levels | CIR Ruling | 6 | The Credit Interpretation Request (CIR) to deem the IEQ-12 ‘Internal Noise Levels’ not applicable (NA), as the project is being delivered as a shell and core project, is denied. This Credit is applicable regardless of how the project is delivered. Making this Credit ‘NA’ would require a change in benchmarks to this Credit.
| x | x | x | x | x |  | x | 2008-12-01 |  | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 7 | As-Built projects that have been previously awarded points for these credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credit (i.e. same shape floor plan, same glazing propoerties and floor-to-ceiling height) can submit a letter from the relevant consultant in place of an as-built model (the as-built drawings must still be provided). The letter must describe the extent of any changes and state the maximum impact they may have on the building performance if it were remodelled. In this case the number of points achieved in the Design rating will automatically be awarded. Please note: Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Modelling must account for worse case scenario; please see the assumptions clarification for more information.
[7 empty] | x | 2009-10-01 |  |  |  | IEQ-7 | Internal Noise Levels | Withdrawn | 8 | This ruling has been withdrawn as of 01-Nov-13. The Credit Criteria states: - The floor construction above habitable rooms of adjacent dwellings (i.e. floor cover) results in an impact isolation standard of Ln,w+Cl ≤ 55. It should state: - The floor construction above habitable rooms of adjacent dwellings (i.e. floor cover) results in an impact isolation standard of Ln,w-Cl ≤ 55. "
[7 empty] | x | 2009-10-01 |  |  |  | IEQ-7 | Internal Noise Levels | Technical Clarification | 9 | Commissioning measurements shall be conducted in at least 10% of the spaces in the building. The range of measurement locations shall be a representation of all the spaces for which credits are available.
[6 empty] | x |  | 2012-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 10 | The inclusion of the words "industrial space" in the credit criteria for the additional point for this credit is incorrect. The credit criteria should read as follows: An additional point is awarded where the sound insulation between acoustically sensitive rooms complies with Dw + LAeq,T > 75.
|  |  |  | x | x | x |  | 2012-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 11 | Fume cupboards do not need to included in the acoustic testing required to demonstrate compliance with the 'Internal Noise Levels' credit. Fume cupboards are activity based noise sources and are therefore not ‘constant noise sources’. Section 1 (Scope) of AS/NZS 2107:2000 states: ‘The Standard is applicable to steady-state or quasi-steady-state sounds’ Therefore, fume cupboards fall outside the intended scope of noise sources for AS/NZS 2107:2000.
| x | x |  | x |  |  |  | 2012-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 12 | The two points available for this credit can be claimed independently of each other. Either the first point, or the second point, or both may be claimed.
x | [7 empty] | 2012-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 13 | To demonstrate compliance with this credit, it is acceptable for project teams to perform the acoustic testing outside of standard operational hours. This is acceptable when an Acoustics Professional confirms that: - All relevant external noise sources which could be expected during a standard operating day are present. This includes traffic and pedestrian noise; and - All relevant internal noise sources which could be expected during a standard operating day, with the exception of those caused by occupants, are present. This includes building services noise. The confirmation from the Acoustics Professional is not required where the acoustic testing is performed one hour before or one hour after core operational hours.
x | [7 empty] | 2012-08-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Technical Clarification | 14 | The noise levels provided within the credit criteria for IEQ-10 'Internal Noise Levels' should be used as upper limits. As such the credit criteria should read: "One point is awarded where it is demonstrated that ambient internal noise levels are less than 45 dBLAeq in general offices and less than 40 dBLAeq in private offices, with the tenancy ready for occupancy but unoccupied as per AS/NZS 2107:2000 'Acoustics - Recommended Design Sound Levels and Reverberation Times for Building Interiors; AND Where a reverberation time (RT60) of less than 0.6 seconds for general offices and a RT60 of less than 0.8 seconds for private offices is achieved"
|  |  | x |  |  |  |  | 2013-11-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Correction | 15 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Tender Drawings Furthermore, the following documentation is being modified: * Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Describing all relevant noise sources; - Describing the design features required to demonstrate that the Credit Criteria has been achieved; and - Stating that the design features have been included in the tender documentation. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Documentation (As Built) | B | The Short Report and the Extract(s) from the Commissioning Report must show that the commissioning agent was present at the time of the acoustic testing, and state that the plant was fully in operation when the tests were carried out.
[7 empty] | x | 2013-11-01 | IEQ-10 | IEQ-12 | IEQ-12 | IEQ-7 | Internal Noise Levels | Documentation (Design) | C | The following documentation is no longer required at the time of a Green Star – Design submission for this credit: • Manufacturer’s data sheet detailing the acoustic properties of the material used in the wall, ceiling floor construction.
x | x | x | x | x | x | x | x |  | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds
| x | [8 empty] | IEQ-13 |  |  | Volatile Organic Compounds | Withdrawn | 1 | Refer to Technical Clarification No.15 The criteria for VOC content of paint in IEQ-13 'Volatile Organic Compounds' refers only to paint applied on site (e.g., excludes paint applied at a factory). It applies to ALL paint applied on site, whether it is exposed or concealed, internal or external.
| x | [6 empty] | 2006-06-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 2 | The table of VOC content criteria is for latex-based paint only - the only criteria for all solvent-based paint is that it must not exceed 200g/l in VOC content.
| x | [6 empty] | 2006-06-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 3 | For paints, adhesives and sealants, the credit assesses the VOC content of the products, not emissions - hence the number of layers is irrelevant.
| x | [6 empty] | 2006-06-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 4 | The credit assesses as-applied paint - hence the documented content must be inclusive of tints.
x | x | [6 empty] | 2006-06-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | CIR Ruling | 5 | 95%, not 100% of all sealants/adhesives must comply with the Credit Criteria.
| x | [6 empty] | 2007-12-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Withdrawn | 6 | Refer to Technical Clarification No.15 As per the current wording of the Technical Manual, paint for both internal and external applications on site must comply with the Credit Criteria.
x | x | [6 empty] | 2007-12-01 | IEQ-11 | IEQ-13 |  |  | Volatile Organic Compounds | CIR Ruling | 7 | The only type of flooring that the credit currently addresses is carpet. Projects may claim this credit for all flooring in the project if all flooring meets the Credit Criteria that is currently stipulated for carpet.
x | x | x | x | x | x | x | x | 2007-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 8 | Reused items/products are not addressed by this credit and do not need to demonstrate compliance with the Credit Criteria.
x | x | [6 empty] | 2007-12-01 | IEQ-11 | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 9 | It must be clear that the evidence accounts for all uses of the relevant product(s) in the project, i.e. via using ‘all’ in the specification or, where appropriate, providing a summary table listing all uses and the attributes of the material(s) used.
| x | [6 empty] | 2008-01-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 10 | Paints, sealants and adhesives used in car parks (internal / external) do not require documentation and are excluded from this credit.
| x | x | x | x | x | x | x | 2008-01-01 |  | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | CIR Ruling | 11 | The Credit Interpretation Request (CIR) to provide a letter from the architectural practise manager (stating that low-VOC paints were used) instead of the inclusion of VOC levels within the specification is denied. The two are not considered equivalent.
| x | x | x | x | x | x | x | 2008-03-01 |  | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 12 | A sealer for an exposed concrete floor must comply with the criteria for an ‘interior sealer’.
x | x | x | x | x | x | x | x | 2008-04-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 13 | Tapes can be excluded from ‘Volatile Organic Compounds’ for all applications.
x | x | [6 empty] | 2008-04-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 14 | Any applications/products for adhesives and sealants that are not identified (e.g. fire, acoustic or water proofing sealants) in the matrix, should be considered architectural sealants and the relevant threshold of 250 g/litre applies.
x | x | x | x | x | x | x | x | 2008-06-01 |  | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 15 | The GBCA continues to receive feedback that supports the removal of the Technical Clarification for Green Star - Office Design and Green Star - Office As Built v2 and Office Interiors v1.1 which states that: “the criteria for VOC content of paint in IEQ-13 'Volatile Organic Compounds'…applies to ALL paint applied on site, whether it is exposed or concealed, internal or external.” The ruling as it is currently worded does not accurately reflect the intent of its original purpose. The intended clarification was mean to communicate the following: This credit applies to ALL paint, - Applied on site; - Whether it is exposed or concealed; and - Whether the paint is classified for internal or external applications.
x | x | x | x | x | x | x | x | 2008-06-01 |  | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 15 | This clarification is now replaced with the following: “Paints, sealants and adhesives used in exterior applications do not require documentation and are excluded from this credit. All internal applications must meet the Credit Criteria, whether they are exposed or concealed, and whether the paint applied internally is classified for internal or external applications” This revision is based primarily on the grounds that the credit category is Indoor Environment Quality (IEQ), and paints used in external applications are not relevant to Indoor Air Quality. Please note that a number of clarifications exist for this credit with regards to the applicability of this credit to areas of the building, such as carparks. These will still apply.
x | x | x | x | x | x | x | x | 2008-08-01 |  | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 16 | All finishes must be accounted for. Where no specific products have been specified, the project team is only required to provide the VOC content limit for all finishes. Where actual products have been specified, the project team is required to provide both the total VOC content limits in the relevant specifications (in case of future addenda) and the VOC content of the actual product in the form of product datasheets.
| x | [6 empty] | 2008-09-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 17 | If a paint (regardless of whether it is classified for interior or exterior applications) is applied on an internal surface, it must be included in the calculations for the 95% of all painted surfaces if the project wishes to claim the credit.
| x | [6 empty] | 2008-09-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 18 | A fully enclosed plant room is considered part of the interior of a building. The internal painted surfaces of such a room must be included in the calculations if the project wishes to claim the credit. However, if the plant room is located on a roof and is semi-exposed then it is not considered to be part of the interior and the painted surfaces can be excluded from this credit.
x | x | x | x | x | x | x | x | 2008-10-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Withdrawn | 19 | This Clarification was withdrawn on 01-Jul-12 and replaced by Technical Clarification #60. Carpets and Flooring: Current GreenGuard Children & Schools® certification is acceptable evidence for demonstrating compliant TVOC levels for flooring other than carpet within the credit criteria where no carpet has been installed and projects wish to use low-VOC flooring. Allowable TVOC limits applicable to GreenGuard Children & Schools® certification, for purposes of flooring materials other than carpet in Green Star: (e.g. hard and resilient flooring <0.22 mg/m³). GreenGuard certification is awarded on a ‘pass/fail’ basis determined according to ASTM standards D-5116-06 and D-6670-01 and the U.S. Environmental Protection Agency's testing protocol for furniture. (www.greenguard.org) As paint, sealants and adhesives also apply to building services, projects must submit all relevant clauses from services specifications (i.e. mechanical, electrical, fire, hydraulics, communications) to preempt Assessors’ clarifications.
| x | [6 empty] | 2008-10-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 20 | Finishes Schedules (if provided in addition to the Specifications) must reflect the requirements of the Specifications. Where discrepancies exist, Manufacturers’ Data Sheets need to be provided to ensure consistency.
| x | [6 empty] | 2008-10-01 |  | IEQ-13 |  |  | Volatile Organic Compounds | Withdrawn | 21 | This clarification was incorrectly placed in this credit The unit of measurement presented in Table IEQ-14.1 in relation to DIM EN 717-1 is ‘mg/m³hr’ and is incorrect. The correct unit of measurement for this test protocol is ‘mg/m³’. Similarly the unit referenced for DIN EN 717-2 should be ‘mg/m²hr’ and not ‘mg/m³hr’ (may be represented as ‘mg/m²/hr’).
x | [7 empty] | 2007-12-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 22 | While all tenant-installed partitions (including the stud-and-gypsum partitions constructed on site) are to be included in the 'Walls & Partitions' Calculator, only the prefabricated partitions should be considered for this credit.
x | [7 empty] | 2008-03-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 23 | The testing methods for tenancy fitout items have been expanded to include both small chamber and large chamber protocols. The product(s) must comply with the maximum TVOC limits in the Fitout VOC Limits tab in this spreadsheet. See the Fitout VOC Limits table for more information
x | [7 empty] | 2006-06-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Withdrawn | 24 | Refer to IEQ-11 No.14, No.15, No.16 This clarification applies to Paint only The criteria for VOC content of paint in IEQ-11 'Volatile Organic Compounds' refers only to paint applied on site (e.g., excludes paint applied at a factory). It applies to ALL paint applied on site, whether it is exposed or concealed. The table of VOC content criteria is for latex-based paint only; the only criteria for all solvent-based paint is that it must not exceed 200g/l in VOC content. The credit assesses the VOC content, not emissions, hence the number of layers is irrelevant. The credit assesses as-applied paint, hence the documented content must be inclusive of tints.
x | [7 empty] | 2006-06-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 25 | This clarification applies to Fitout Items only 95%, not 100% of fitout items must comply with the Credit Criteria. Only tenant-installed, demountable/modular partitions must be included in the calculations.
x | [7 empty] | 2008-09-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 26 | If a paint (regardless of whether it is classified for interior or exterior applications), is applied on an internal surface, it must be included in the calculations for the 95% of all painted surfaces if the project wishes to claim the credit.
x | [7 empty] | 2008-10-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 27 | Ruling updated September 2013 to reflect Greenguard name changes. Tenancy Fitout Items: Current UL GREENGUARD (previously known as GreenGuard Indoor Air Quality®*) and UL GREENGUARD GOLD (previously known as GreenGuard Children & Schools®*) certifications are acceptable evidence for demonstrating compliant TVOC levels within the credit requirements for tenancy fitout items. Allowable TVOC limits applicable to UL GREENGUARD and UL GREENGUARD GOLD certification, for purposes of Green Star: (Workstations, Walls, Partitions, Tables and Storage Units <0.5 mg/m³); (Chairs <0.25mg/m³). UL GREENGUARD certification is awarded on a pass/fail basis determined according to ASTM standards D-5116-06 and D-6670-01 and the U.S. Environmental Protection Agency's testing protocol for furniture. (www.greenguard.org) *NB certification under either the old, or new, name will be accepted if valid at the time of Green Star project registration.
|  | x |  | x | x | x | x | 2008-09-01 |  |  | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 28 | All registered projects must include the exempt compounds (based on ASTM D3960 as well as SCAQMD Rule 1168), in the TVOC calculations. The exemption for those compounds in the Standards is based on the impact that they have on air pollution, not indoor environment quality (i.e. if the VOC compound did not participate in air pollution reactions, it was exempted from the VOC content). A practice in the industry exists to replace non-exempt compounds (e.g. methyl ethyl ketone) with "exempt compounds" (e.g. acetone) in formulations of paints, coatings and adhesives. While this lowers the TVOC content of the product, it will still have an indoor environment impact. For this reason exempt compounds must be included in TVOC calculations submitted.
x | x | x | x | x | x | x | x | 2008-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 29 | The tables in the Paints and Adhesives tab supersede the Paint and Adhesive & Sealant VOC Levels in the following Green Star rating tools. - Green Star - Office Design v2 - Green Star - Office As Built v2 - Green Star - Office Interiors v1.1 Except for the addition of the first item to the Paints table ("Walls and Ceilings - interior gloss"), the tables within the Green Star - Office v3, Green Star - Retail Centre v1 and Green Star - Education v1 Technical Manuals are not altered by this clarification. All projects registered after 20/11/2008 must comply with correction. All projects registered before this date has the following options: 1) Projects can choose whether they wish to follow the tables below; OR 2) the tables in the current Technical Manual Project teams cannot combine elements from both tables to support their submission.
x | x | x | x | x | x | x | x | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Withdrawn | 30 | See Technical Clarification No. 40 Theoretical VOC calculations, based on the subtotal of the known VOC values of the product’s raw material components, for adhesive, sealants, or paints can be submitted as evidence for this credit. Project teams must submit a signed letter from the manufacturer listing the VOC results and stating that the calculations have been performed as above. This document substitutes the requirement for test reports or a manufacturer’s data sheet. All other documentation stated in the Technical Manual is required.
x | x | x | x | x | x | x | x | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | withdrawn | 31 | This clarification was originally posted in Dec-08. Please refer to TC No. 44 for more information. Waterproofing membranes, applied in wet areas, are categorised under Sub Category ‘Any solvent-based coatings whose purpose is not covered in table’ (Table IEQ-13.1 in ODv3 Technical Manual).
x | x | [6 empty] | 2008-12-01 | IEQ-11 | IEQ-13 |  |  | Volatile Organic Compounds | Technical Clarification | 32 | Projects may refer to the Total Volatile Organic Compound (TVOC) information contained within the Additional Guidance section of the Green Star – Office v3 Technical Manual
x | x | x | x | x | x | x | x | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Withdrawn | 33 | See Technical Clarification No. 40 A VOC data sheet is defined as: - A testing certificate issued by a NATA or ISO/IEC 17025 certified testing laboratory. This test certificate must state the product name, TVOC result and the compliant testing method used. OR - Where Adhesives product MSDS (Material Safety Data Sheet) includes TVOC information. The MSDS must include the test method against which the result was obtained along with the numerical result expressed in g/l of product. OR - Where Paint TVOC has been calculated from the TVOC data for the raw materials, manufacturers can produce a written statement signed by a suitable company representative that outlines the calculation method used to determine the TVOC level of the product, along with the TVOC result expressed in g/l of ready to use product.
x | x | x | x | x | x | x | x | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Correction | 34 | Underlay must be included in the carpet product VOC calculations for this credit. Carpet underlay products are to comply with the emission limits stated in ‘Table IEQ-13.3; Carpet TVOC emissions limits’ of the Technical Manual.
x | x | x | x | x | x | x | x | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 35 | For the purposes of Green Star, PVA can be categorized as laminate adhesives. Although not stated in Interiors v1.1, the Adhesives & Sealants table in Office Design v3 has an expanded name under product type ‘Wood Flooring Adhesives’ to include ‘Laminate Adhesives’. Hence, for the purposes of IEQ-11, please categorise PVA under the product type ‘Wood Flooring Adhesives’.
x | x | x | x | x | x | x | x | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Withdrawn | 36 | This clarification was originally posted on March-09. See Technical Clarification No. 46 for more information. Glazing Adhesive film - VOC levels provided in table IEQ-13.2 in relation to Architectural Sealants (i.e. 250 g/l) also applies to glazing film that is installed on office fitout interior glazing. The requirements apply to the adhesive used in these films rather then to the entire finished product including both the film and adhesive.
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 37 | Fitout items include tables, chairs and desks as per page 110 of the technical manual; walls/partitions and storage units are not included.
x | x | x | x | x | x | x | x | 2009-03-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 38 | Acoustic Sealants must be categorised under the Product Type 'Architectural Sealants' (with a Max VOC Content limit of 250 g/litre).
x | x | x | x | x | x | x | x | 2009-03-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 39 | Adhesives and mastics that are used for temporary formwork are not required to comply with Green Star VOC credit criteria. Such materials are not commonly used within enclosed spaces, and as such, the impact on the indoor environment quality of the completed project is negligible.
x | x | [6 empty] | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Correction | 40 | For the purposes of Green Star, a VOC data sheet is defined as: - Laboratory test reports or test certificates – Product TVOC test reports/certificates must be issued by a NATA or ISO/IEC 17025 certified testing laboratory and must state the product name, TVOC result and the testing method used. Refer to the Additional Guidance section of the Green Star VOC credit for lists of compliant test methods. OR - Material Safety Data Sheets (MSDS) – Where a product MSDS includes TVOC information, it must include the numerical result expressed in g/litre of product and the test method used to obtain the results. Refer to the Additional Guidance section of the Green Star VOC credit for lists of compliant test methods. OR - Manufacturer prepared VOC data sheets – Product VOC data sheets that have been prepared by the manufacturer to demonstrate TVOC must be based on theoretical calculations of the subtotal of the known VOC values of the product’s raw material components. Where the TVOC content of individual components is not known, it must be determined experimentally by one of the appropriate test methods listed in the Additional Guidance section of the Green Star VOC credit. Theoretical TVOC calculations prepared by manufacturers may be submitted as evidence for compliance with the credit. Project teams must submit a signed letter from the manufacturer containing the following: - Numerical TVOC results expressed in g/litre of product; - Manufacturer’s statement that the results have been obtained based on the subtotal of the known VOC values of the product’s raw material components.
|  | x | x | x | x | x | x | 2008-12-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 40 | For the purposes of Green Star, a VOC data sheet is defined as: - Laboratory test reports or test certificates – Product TVOC test reports/certificates must be issued by a NATA or ISO/IEC 17025 certified testing laboratory and must state the product name, TVOC result and the testing method used. Refer to the Additional Guidance section of the Green Star VOC credit for lists of compliant test methods. OR - Material Safety Data Sheets (MSDS) – Where a product MSDS includes TVOC information, it must include the numerical result expressed in g/litre of product and the test method used to obtain the results. Refer to the Additional Guidance section of the Green Star VOC credit for lists of compliant test methods. OR - Manufacturer prepared VOC data sheets – Product VOC data sheets that have been prepared by the manufacturer to demonstrate TVOC must be based on theoretical calculations of the subtotal of the known VOC values of the product’s raw material components. Where the TVOC content of individual components is not known, it must be determined experimentally by one of the appropriate test methods listed in the Additional Guidance section of the Green Star VOC credit. Theoretical TVOC calculations prepared by manufacturers may be submitted as evidence for compliance with the credit. Project teams must submit a signed letter from the manufacturer containing the following: - Numerical TVOC results expressed in g/litre of product; - Manufacturer’s statement that the results have been obtained based on the subtotal of the known VOC values of the product’s raw material components.
x | x | x | x | x | x | x | x | 2009-07-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 41 | As per the Green Star – Office Interiors v1.1 Technical Manual, under additional guidance, a product certified under the GECA 23-2005 ‘Architectural and Protective Coatings’ (Formerly AELA 23-2005), would meet the requirements of this credit. As such, products certified under this standard can present the GECA certificate in lieu of “VOC data sheets that detail the VOC level of each product for which points are claimed”. For Office v2 and Office Interiors v1.1, this clarification applies to all applications as stated in the paints section of this credit in the Technical Manual. For all other tools, this clarification applies to all applications except for “Timber and binding primers”, “One and two pack performance coatings for floors” or “Any solvent-based coatings whose purpose is not covered in table” as these applications are not covered by the above mentioned standard.
x |  |  |  | x | x |  | x | 2007-12-01 | IEQ-11 |  |  |  | Volatile Organic Compounds | Technical Clarification | 42 | While all tenant-installed partitions (including the stud-and-gypsum partitions constructed on site) are to be included in the 'Walls & Partitions' Calculator, only the prefabricated partitions should be considered for this credit.
x | x | x | x | x | x | x | x | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 43 | PVC pipe cements - Pipe cements are not relevant to the VOC credit as they have little influence on indoor air quality. Plumbing pipes are usually installed some time prior to building occupation and any residual of solvent will be negligible by the time the building is sealed and occupied. In addition plumbing pipes are not a major component of an individual fitout or building, plumbing cements are minor in quantity in the indoor fitout when compared to adhesives used in countless other indoor applications.
x | x | x | x | x | x | x | x | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | correction | 44 | Waterproofing membranes are included in the ‘Architectural Sealant’ category of table IEQ-13.2
X | [7 empty] | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 45 | The requirements of the Volatile Organic Compounds credit in Green Star rating tool pertaining to fitout items relates to the contribution of that (whole) item to the release of volatile organic compounds in the indoor environment. While a product's component may display a low VOC potential, it is the actual numeric contribution of the whole item that is under consideration by the credit. This may include adhesives and coatings applied to the finished item, as well as VOC emissions from components.
x | x | x | x | x | x | x | x | 2009-10-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 46 | Glazing Film is excluded from this credit
x | x | x | x | x | x | x | x | 2010-03-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 47 | Carpet certified by the Carpet Institute of Australia Limited Environmental Certification Scheme (CIAL ECS) at level 2, 3 or 4 are deem to satisfy the requirements of the credit for carpets. The certification licence for the product current at the time or project registration is the means to demostrate compliance via this option. See: http://www.gbca.org.au/green-star/materials-category/product-and-forest-certification-schemes/1616.htm for more information.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Correction | 48 | The documentation requirement for a 'Extract(s) from the specifications is corrected, the following is required: Extract(s) from the specification(s): • Nominating the TVOC limits for each product within the relevant category type; • Nominating the compliant test methods for demonstrating VOC limits • Stating that the contractor is required to obtain approval of the design team or client before substituting the finishes listed in the schedule; • Requiring that at the end of construction works, the contractor undertakes a final audit to ensure that the correct products have been used; and • Where the project has no products from a particular category, showing where it is stipulated that no such product is to be used in the project.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 49 | Fitout items certified by the Australasian Furnishing Research and Development Institute, Sustainability Standard for Commercial Furniture - AFRDI Standard 150 September 2010, at level A, B or C, are deemed to meet the criteria for the fitout items. The certification licence for the product, current at the time of project registration, is the means to establish compliance via this option.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 50 | Fitout items and Carpets or other flooring certified by the following Good Environmental Choice Australia Standards, are deemed to meet the criteria for the carpet, other flooring or fitout items. • GECA 28-2010 v2 - 'Furniture and Fittings'; • GECA 50-2010 v2 - 'Carpets' ; • GECA 25-2010 v2 - 'Floor Coverings' ; The certification licence for the product current at the time or project registration is the means to demostrate compliance via this option. It should be noted that items certified under the standards listed below do not meet the credit criteria as these standards do not describe VOC limits: GECA 31-2006; GECA 07-2006; GECA 30-2006, GECA 25-2005 'Floor coverings', and GECA 28-2006 v1.1 (Modified 2010)
x | x | x | x | x | x | x | x | 2011-02-22 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Correction | 51 | Fitout items certified by the Ecospecifier's GreenTag GreenRate v3, under four Supplementary Category Specific Standards - 'Carpet and Flooring Supplementary Standard', 'Furniture Supplementary Standard', 'Joinery Supplementary Standard' and 'Walls, Partitions and Ceilings Supplementary standard’ at level A or B (Level C excluded), are deemed to meet the criteria for carpets, other flooring or fitout items. The certification licence for the product current at the time or project registration is the means to demonstrate compliance via this option.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compound | CIR Ruling | 52 | For carpets and laminate floor coverings, an option for demonstrating compliance with TVOC levels is as follows: ISO 10580 (also known as ISO/TC 219) – Document N238 – Resilient, Textile and Laminate Floor Coverings Evaluation of Volatile Organic Compounds Emissions, with a limit of 500μg/m2/hr at 24 hours.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compound | Technical Clarification | 55 | For floor coverings (other than carpet), an option for demonstrating compliance with TVOC levels is as follows: ISO16000 parts 9, 10 and 11 (also known as the EN 13419), with a TVOC limit at three days of 5mg/m²/h and 0.5mg/m²/h at 28 days.
x | [7 empty] | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Withdrawn | 56 | Withdrawn 01-Jul-12 and replaced by correction #61. 95%, not 100% (by area), of all carpets must comply with the credit criteria.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compound | Technical Clarification | 57 | Carpet or other flooring installed as part of the base building works prior to fitout works, can be deemed re-used for the purpose of this credit. As documentation: Provide a letter from either the building manager, leasing agent or building owner stating that the carpet in the fitout was installed as part of base building works.
x | x | x | x | x | x | x | x | 2012-08-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compound | Technical Clarification | 58 | As Built Documentation for this credit requires confirmation from a subcontractor that a particular item or product was used or installed on site. Confirmation of this information from the head contractor is also acceptable.
x |  |  |  | x | x | x |  | 2012-08-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compound | Technical Clarification | 59 | Fitout items - Whole item emissions certificate, not product components Accredited laboratories will issue a TVOC certificate for a product or a range of products (based on a representative sampling basis). This is the VOC data sheet required by the credit for fitout items. It is not possible to calculate the TVOC of a fitout item by summing the result of testing for all components. The complexity in doing this arises from the surface area of various components in various items. Accredited laboratories are able to perform this calculation once all product components have been tested and based on drawings of the item showing dimensions. The fitout item criteria of the credit apply to finished items, meaning laboratories will require testing of all components. Where the manufacturer or supplier of a component has already tested a component, laboratories will not need to retest these. Laboratories will require a letter of authorization to use the test certificate and test results from the owner of the certificate. Representative sampling for a range of products entails testing of all the products that are the worst emitters, and applying that result across a range of products with a range of finishes or optional components. This scenario will only work where the full range of components is stated. In the case of upholstered fitout items this entails specific ranges of textiles that are taken into account in the TVOC certificate. Some GBCA recognised product certification standards include such requirements and are therefore recognised as providing compliance to the credit criteria for fitout items. See http://www.gbca.org.au/green-star/materials-category/product-certification-schemes/2933.htm for detail.
x | x | x | x | x | x | x | x | 2012-08-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Technical Clarification | 60 | Ruling updated September 2013 to reflect Greenguard name changes. Carpets and Flooring and Tenancy Fitout Items: Current UL GREENGUARD GOLD (previously known as GreenGuard Children & Schools®*) certification is acceptable evidence for demonstrating compliant TVOC levels for flooring other than carpet. Current UL GREENGUARD (previously known as GreenGuard Indoor Air Quality®*) and UL GREENGUARD GOLD (previously known as GreenGuard Children & Schools®*) certifications are acceptable evidence for demonstrating compliant TVOC levels within the credit requirements for tenancy fitout items. UL GREENGUARD certification is awarded on a pass/fail basis determined according to ASTM standards D-5116-06 and D-6670-01 and the U.S. Environmental Protection Agency's testing protocol for furniture. (www.greenguard.org). *NB certification under either the old, or new, name will be accepted if valid at the time of Green Star project registration.
x | [7 empty] | 2012-08-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Correction | 61 | 95%, not 100%, of carpet and carpet underlays (by area) used in internal applications must comply with the Credit Criteria.
|  | x | x | x | x | x | x | 2009-03-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Extract(s) from the specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Volatile Organic Compounds | Documentation (As Built) | B | Where the point for carpets is claimed as N/A, projects can substitute the Confirmation from the Contractor with a Confirmation from the Architect stating that no carpet was used in the project.
x | x | x | x | x | x | x | x |  | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 1 | Refer to Clarification No. 22 E1 or E0 limit under AS/NZS 2269:2004, testing procedure AS/NZS 2098.11 for plywood is acceptable means of compliance with the Credit Criteria.
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 2 | Refer to Clarification No. 20 E1 and E0 are commonly-known terms in the building and fit-out industry and are recognised in Green Star- Office Design v2 according to 'rate-based' as well as 'concentration-based' emission testing results.
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 3 | Refer to Clarification No. 22 'Rate-based' Standards / Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: ASTM D5116, EN 13419, DIN EN717-2 and JIS A 1901
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 4 | Refer to Clarification No. 22 Products demonstrating formaldehyde emission 'rates' of less than or equal to 0.100 +/- 0.005 mg/ m²/hr are compliant for this credit. (This is the equivalent to a rating of less than or equal to E1).
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 5 | Refer to Clarification No. 22 E1 and E0 as 'rate-based' emission results are defined as: E1: 0.060 to 0.100 +/- 0.005 mg/m2/hr; E0: less than or equal to 0.050 +/- 0.005 mg/m2/hr.
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 6 | Refer to Clarification No. 22 'Concentration-based' Standards and Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: - AS/NZS 2269:2004, testing procedure AS/NZS 2098.11:2005 method 10 for plywood; - AS/NZS 1859.1:2004 - particle board, with use of testing procedure AS/NZS 4266.16:2004 method 16; - AS/NZS 1859.2:2004 - dry processed fibreboards (MDF), with use of testing procedure AS/NZS 4266.16:2004 method 16; - JIS A 5908:2003- Particleboard and Plywood, with use of testing procedure JIS A 1460; and - JIS A 5905:2003 - dry processed fibreboards (MDF), with use of testing procedure JIS A 1460
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 7 | Refer to Clarification No. 22 Products demonstrating formaldehyde 'concentration' emission rates of less than or equal to 1.0mg/L (<1 part per million) are compliant for this credit. (This is the equivalent to a rating of less than or equal to E1)
| x | x | x | x | x | x | x | 2006-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 8 | Refer to Clarification No. 22 'Concentration-based' emission results are defined by AS/NZS 1859:2004 as: E1: 1 mg/L to .6 mg/L E0: less than or equal to 0.5 mg/L
x | x | [6 empty] | 2006-09-01 | IEQ-12 | IEQ-14 |  |  | Formaldehyde Minimisation | Withdrawn | 9 | Refer to Clarification No. 22 DIN EN 717-2 (not DIN EN 717-1) complies with the Credit Criteria because it provides 'rate-based' emission results which enable calculation of net-best air quality that meets best human exposure standards (reported in mg/m2/h ). DIN EN 717-1 measures emissions by chamber testing but reports in mg/m3. This does not meet the Credit Criteria because the cubic metre measurement of the chamber space in which the products are tested do not correspond to the differing cubic metre measurements of the actual space in which a product will be placed.
x | x | x | x | x | x | x | x | 2007-12-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 10 | Refer to Clarification No. 22 JIS A 5908:2003-Particleboard is appropriate for meeting the Credit Criteria, as JIS A 5908 for additional product types would be.
x | x | x | x | x | x | x | x | 2007-12-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 11 | This credit addresses all composite wood products, including plywood, particleboard and MDF.
x | x | x | x | x | x | x | x | 2007-12-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 12 | Reused items are not addressed by this credit and do not need to demonstrate compliance with the Credit Criteria.
x | x | [6 empty] | 2007-12-01 | IEQ-12 | IEQ-14 |  |  | Formaldehyde Minimisation | Technical Clarification | 13 | It must be clear that the evidence accounts for all uses of the relevant material in the project, i.e. through using the word ‘all’ in the specification or, where appropriate, providing a summary table listing all uses and the attributes of the material(s) used.
x | x | x | x | x | x | x | x | 2008-02-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 14 | Products made completely of laminate which are not pressed onto a wood-product substrate (e.g. High-Pressure Laminate and Compact Laminate), are not considered to be composite wood products and are therefore not subject to the formaldehyde minimisation credit in Green Star rating tools.
| x | [6 empty] | 2008-01-01 |  | IEQ-14 |  |  | Formaldehyde Minimisation | Withdrawn | 15 | Refer to Clarification No. 22 Duplicate clarification See clarification number 14 within this credit
| x | x | x | x | x | x | x | 2008-01-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 16 | The following applications are not addressed by this credit and are therefore not subject to its Credit Criteria: - Any composite wood products used in exterior applications (e.g. decorative façade); - Formwork; - Internal car park applications; - Reused composite wood products; and - Raw timber.
| x | x | x | x | x | x | x | 2008-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 17 | Refer to Clarification No. 22 The GBCA does not define E1 and E0 according to AS4266.16 (2004) as this is purely a test protocol for determining formaldehyde in particleboard or fibreboard. For the purposes of Green Star the GBCA defines E1, E0 and Super E0 as shown in the IEQ-14 Table tab in this spreadsheet. See the IEQ-14 Table No.1 for more information
| x | x | x | x | x | x | x | 2008-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 18 | Refer to Clarification No. 22 Manufacturers can present ASTM D6007 and ASTM E1333 test results as evidence of compliance with IEQ-14 ‘Formaldehyde Minimisation’. In the case of ASTM D6007, the test report must confirm that the conditions of Table 1 comply for the particular wood product type. In the case of both tests, the final results must be presented in EN 717-2 equivalent, using the correlation ratio of 0.98.
| x | x | x | x | x | x | x | 2008-09-01 |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Withdrawn | 19 | Refer to Clarification No. 22 Test Method DIN EN 717-2 is the German translation of EN 717-2. Evidence referencing DIN EN 717-2 is acceptable evidence under IEQ-14.
x | x | x | x | x | x | x | x | 2008-09-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 20 | The values represented by the E1, E0 and Super E0 titles are defined by the relevant standards both domestically and internationally. As there is no consensus on what the labels measure and what formaldehyde levels for each level are, the test certificate provided within the submission must include the numerical formaldehyde result.
x | [8 empty] | IEQ-12 |  |  |  | Formaldehyde Minimisation | Withdrawn | 21 | Refer to Clarification No. 22 E1 and E0 are commonly-known terms in the building and fit-out industry and are recognised in Green Star- Office Interiors v1.1 according to 'rate-based' as well as 'concentration-based' emission testing results. 'Rate-based' Standards / Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: ASTM D5116, EN 13419, DIN EN717-2 and JIS A 1901 Products demonstrating formaldehyde emission 'rates' of less than or equal to 0.100 +/- 0.005 mg/ m²/hr are compliant for this credit. (This is the equivalent to a rating of less than or equal to E1). E1 and E0 as 'rate-based' emission results are defined as: E1: 0.060 to 0.100 +/- 0.005 mg/m2/hr; E0: less than or equal to 0.050 +/- 0.005 mg/m2/hr. Super E0: less than or equal to 0.040 +/- 0.005 mg/m2/hr
x | [8 empty] | IEQ-12 |  |  |  | Formaldehyde Minimisation | Withdrawn | 21 | Concentration-based' Standards and Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: - AS/NZS 2269:2004, testing procedure AS/NZS 2098.11:2005 method 10 for plywood; - AS/NZS 1859.1:2004 - particle board, with use of testing procedure AS/NZS 4266.16:2004 method 16; - AS/NZS 1859.2:2004 - dry processed fibreboards (MDF), with use of testing procedure AS/NZS 4266.16:2004 method 16; - JIS A 5908:2003- Particleboard and Plywood, with use of testing procedure JIS A 1460; and - JIS A 5905:2003 - dry processed fibreboards (MDF), with use of testing procedure JIS A 1460 Products demonstrating formaldehyde 'concentration' emission rates of less than or equal to 1.0mg/L (<1 part per million) are compliant for this credit. (This is the equivalent to a rating of less than or equal to E1). 'Concentration-based' emission results are defined by AS/NZS 1859:2004 as:
x | [8 empty] | IEQ-12 |  |  |  | Formaldehyde Minimisation | Withdrawn | 21 | E1: 1 mg/L to .6 mg/L E0: less than or equal to 0.5 mg/L Super E0: less than or equal to 0.3 mg/L is only recognised in the F4Star benchmark in the Japanese Standard JIS A 5905:2003 - dry processed fibreboards. (Super E0 is not referenced by AS/NZS 1859:2004).E1 or E0 limit under AS/NZS 2269:2004, testing procedure AS/NZS 2098.11 for plywood is acceptable means of compliance with the Credit Criteria.
x | x | x | x | x | x | x | x | 2008-11-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Correction | 22 | The tab "Formaldehyde Emission Limits" within this document summarizes and clears up a number of clarifications on the existing spreadsheet. The table within this tab replaces all emission level tables for this credit released in: - Green Star - Office Design v1 - Green Star - Office As Built v1 - Green Star - Office Design v2 - Green Star - Office As Built v2 - Green Star - Office v3 - Green Star - Retail Centre v1 - Green Star - Education v1 - Green Star - Healthcare Pilot - Green Star - Industrial Pilot - Green Star - Multi-Unit Residential Pilot Please see TC.25 for Green Star - Office Interiors
[8 empty] | 2009-05-01 |  |  |  | IEQ-9 | Formaldehyde Minimisation | withdrawn | M1 | The following Technical Clarification has been withdrawn: “Whilst all other Green Star rating tools refer to E1 board, the Technical Working Group (TWG) for Green Star – Multi Unit Residential PILOT tool, have raised the benchmark to E0 board. Please note that this feedback is acknowledged, and may be used to inform the Green Star - Multi Unit Residential v1 tool.” Multi Unit Residential PILOT projects must instead comply with the numerical limit stipulated in IEQ-9 Formaldehyde Minimisation Correction no.22 (Formaldehyde Emission Limits table) to claim this credit.
| x | [6 empty] | 2008-12-01 |  | IEQ-14 |  |  | Formaldehyde Minimisation | Correction | 23 | Under Compliance Requirements for Green Star – Office As-Built IEQ-14 Formaldehyde Minimisation, the documentation required requests that: “VOC data sheets for each product used which quote the VOC content of the product provided by the supplier and signed by a suitably qualified representative are necessary”. As this is the evidence requirement for Green Star – Office As-Built IEQ-14, this should read: “Formaldehyde emissions report(s) for each product used which quote the Formaldehyde content of the product, provided by the supplier and signed by a suitably qualified representative are necessary”.
x | x | x | x | x | x | x | x | 2008-12-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 24 | The Compliance Requirements in this credit state that: Rate-based Standards / Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: ASTM D5116, EN 13419, DIN EN717-2 and JIS A 1901 This should read: Rate-based Standards / Testing Methods recognised as acceptable means of compliance with the Credit Criteria include: ASTM D5116, ISO 16000 part 9, 10 and 11(known in Europe as EN 13419), DIN EN717-2 and JIS A 1901
x | [7 empty] | 2008-11-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Correction | 25 | The tab "OI IEQ-12 Formaldehyde" within this document summarizes and clears up a number of clarifications on the existing spreadsheet. The table within this tab replaces all emission level tables for this credit released in: - Green Star - Office Interiors v1.1
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Correction | 26 | 95% (by area), not 100%, of all composite and engineered wood products must comply with the credit criteria.
x | x | x | x | x | x | x | x | 2011-01-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 27 | Engineered wood products contained in product certified by all GBCA recognised product certification standards are deemed to meet the credit criteria. Recognised Product certification schemes standards are listed on the GBCA website.The certification licence for the product current at the time or project registration is the means to demostrate compliance via this option.
[8 empty] | 2011-01-01 | IEQ-12 |  |  |  | Formaldehyde Minimisation | Correction | 28 | A new version of IEQ-12 'Formaldehyde Minimisation' has been released for Green Star - Office Interiors. This credit incorporates all the clarifications in this credit applicable to Green Star - Office Interiors v1.1. In addition, it simplifies the documentation requirements for this rating tool. This credit is applicable to all projects registered after December 2010. All clarifications listed after December 2010 apply to the new credit. All clarifications listed prior to December 2010 can be disregarded and are not applicable to the new credit.
x | x | x | x | x | x | x | x | 2012-08-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 29 | As Built Documentation for this credit requires confirmation from a subcontractor that a particular item or product was used or installed on site. Confirmation of this information from the head contractor is also acceptable.
|  |  |  | x | x |  |  | 2013-11-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Technical Clarification | 30 | The GBCA confirms that the scope of this credit includes all fitout items, including loose furniture.
|  | x | x | x | x | x | x | 2009-03-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Documentation (Design) | A | Where the credit is claimed as N/A, projects can substitute the Extract(s) from the specification(s) with a Confirmation from the Architect stating that no engineered wood products are being used in the project.
|  | x | x | x | x | x | x | 2009-03-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Extract(s) from the specification(s) * Confirmation from the contractor All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 | IEQ-12 | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Minimisation | Documentation (As Built) | C | Where the point for this credit is claimed as N/A, projects can substitute the Confirmation from the Contractor with a Confirmation from the Architect stating that no engineered wood products were used in the project.
| x | x | x | x | x | x |  |  |  | IEQ-15 | IEQ-15 | IEQ-10 | Mould Prevention
| x | [6 empty] | 2006-01-01 |  | IEQ-15 |  |  | Mould Prevention | Technical Clarification | 1 | This credit stipulates an active humidity control system. Systems that rely on humidity monitoring only or humidity control by virtue of coil selection only do not satisfy the Credit Criteria and will not be rewarded. The second item under the Compliance Requirements for spaces in the building which are mechanically ventilated should read "A copy of the selection of the mechanical specification where the system design parameters in terms of design conditions, humidity and temperature and humidity control parameters are stipulated".
| x | [6 empty] | 2009-03-01 |  | IEQ-15 |  |  | Mould Prevention | Technical Clarification | 2 | For Mixed Mode Buildings both modes of operation must satisfy the relevant mechanical and natural ventilation criteria.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-15 | IEQ-15 | IEQ-10 | Mould Prevention | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is naturally ventilated and meets the requirements of IEQ-1 'Ventilation Rates', this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-15 | IEQ-15 | IEQ-10 | Mould Prevention | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *As built architectural drawings All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | IEQ-15 | IEQ-15 | IEQ-10 | Mould Prevention | Documentation (As Built) | B | For Mechanically air-conditioned spaces, the Extract(s) from the Commissioning Report must show that testing occurred using the range stated in the control system and demonstrate that all valves, dampers, fans, and the rest of the equipment, work as intended.
x | x | x |  |  | x | x |  |  | IEQ-14 | IEQ-16 | IEQ-16 | IEQ-16 | Tenant Exhaust Riser / Tenant Exhaust
| x | x |  |  | x |  |  | 2007-12-01 |  | IEQ-16 | IEQ-16 | IEQ-16 | Tenant Exhaust Riser / Tenant Exhaust | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem discharge louvers on each level equivalent of a provision for a tenant exhaust riser is granted conditionally on the project’s ability to clearly demonstrate the following within the submission: - The quantity and position of the discharge louvers is sufficient to serve all tenants on all floors; and - A fan, wired to the base building board, is provided on each floor to serve all tenancies.
x | [7 empty] | 2007-12-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | Technical Clarification | 2 | To be deemed enclosed, the photocopy room must have full-height partitions on all sides and a door that can be shut.
x | [7 empty] | 2008-03-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | Technical Clarification | 3 | Where supply air is being provided to an enclosed photocopier/print room, the dedicated exhaust riser must be able to exhaust a net 5L/s/m2 over that which is being supplied, and meet all other criteria stated in the Technical Manual.
x | [7 empty] | 2008-03-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to deem an 'almost-enclosed area' with an opening that is similar in size to a door equivalent to an enclosed room is granted. The size of the opening must not exceed 1.2 meters wide x 2.2 meters high (standard door dimensions).
x | [7 empty] | 2008-08-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to have a negatively pressured moderately enclosed room (i.e. a room which is contained by three or more walls, and has an opening that is larger than 1.2 x 2. meters) that is being exhausted per the Technical Manual as shown by a Computational Fluid Dynamics (CFD) model be deemed equivalent to an enclosed room is granted. Please note: This CIR ruling approves the use of CFD modelling to show that a negatively pressured moderately enclosed room can be exhausted as per the Credit Criteria and Compliance Requirements on the Technical Manual. It does not automatically grant the points for this credit.
x | [7 empty] | 2008-08-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | CIR Ruling | 6 | The Credit Interpretation Request to have a print/photocopy cupboard exhaust be provided instead of an enclosed print/photocopy room is granted conditionally. The project must provide evidence that the entire cupboard area is being exhausted as per the Technical Manual. The evidence must include modelling or a smoke trace test demonstrating that the entire open face of the cupboard is being extracted at a rate of 5l/s/m2 (Floor Area Enclosure) or higher, as per AS 1668.2-2002.
x | x | [7 empty] | IEQ-14 | IEQ-16 |  |  | Tenant Exhaust Riser / Tenant Exhaust | Withdrawn | 7 | The following clarification is being deleted as it was incorrectly placed under the wrong credit: Test Method DIN EN 717-2 is the German translation of EN 717-2. Evidence referencing DIN EN 717-2 is acceptable evidence under IEQ-14.
x | [7 empty] | 2008-12-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | Technical Clarification | 8 | Individual printers placed outside a print/photocopy room (i.e. in the general office area), that are not grouped next to other printing equipment, and meet the emissions limits in the IEQ-14 Emission Limits when tested under the requirements of ECMA-328, can be excluded from this credit. Projects must submit test results showing that the selected equipment meets the relevant credit criteria. The test result must show that testing occurred as per ECMA-328.
x | [7 empty] | 2008-12-01 | IEQ-14 |  |  |  | Tenant Exhaust Riser / Tenant Exhaust | Technical Clarification | 9 | Projects which do not have a print/photocopy room and only contan print/photocopy equipment that meets the requirements of ECMA-328 can claim the point for this credit. Test certificates for printer/photocopier equipment must be provided
|  | x | [5 empty] | 2012-08-01 | IEQ-14 | IEQ-16 |  |  | Tenant Exhaust Riser / Tenant Exhaust | Technical Clarification | 10 | Where the credit criteria reads "Has a capacity of 0.35 L/s/m2 for 100% of the NLA on any individual floor", this should be interpreted as "Has take-offs sized to 0.35 L/s/m2 for 100% of the NLA on any individual floor". Therefore, to demonstrate compliance with this credit project teams need to: - Install an exhaust fan which provides 0.2 L/s/m2 for the entire NLA, and; - Size take-offs at each floor for 0.35 L/s/m2 for the NLA of that floor. | Ruling based on query from project GS-942D and discussion with Adrian Carrick and Adriaan Window.
[5 empty] | x | [6 empty] | IEQ-17 | Air Distribution Systems / Air Supply Ductwork
[8 empty] | 2009-03-01 |  |  |  | IEQ-17 | Air Distribution Systems / Air Supply Ductwork | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is naturally ventilated and meets the requirements of IEQ-1 'Ventilation Rates', this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit. | This clarification are already included in the printed version of the Healthcare Mnaual. It can be deleted off the sheet
[8 empty] | 2009-03-01 |  |  |  | IEQ-17 | Air Distribution Systems / Air Supply Ductwork | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Confirmation for the base building manager All other documentation must be provided as per the Technical Manual at the time of submission. | This clarification are already included in the printed version of the Healthcare Mnaual. It can be deleted off the sheet
[8 empty] | 2009-03-01 |  |  |  | IEQ-17 | Air Distribution Systems / Air Supply Ductwork | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Extracts from the specifications All other documentation must be provided as per the Technical Manual at the time of submission. | This clarification are already included in the printed version of the Healthcare Mnaual. It can be deleted off the sheet
[5 empty] | x |  |  | 2013-11-01 |  |  |  | IEQ-17 | Air Distribution Systems / Air Supply Ductwork | Documentation (As Built) | C | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star – As-Built submission for this credit: * Extract from the specifications(s) Instead of Extracts from the specification(s) project teams must submit the following: * Extract(s) from the Commissioning Report showing: - The humidity levels in the ducts and in the occupied space for all modes of operation; and - That the testing occurred using the range stated in the control system and demonstrate that all valves, dampers, fans, and the rest of the equipment, work as intended. All other documentation must be provided as per the Technical Manual at the time of submission.
[5 empty] | x | [6 empty] | IEQ-18 | Outdoor Pollutant Source Control
[5 empty] | x | x | [5 empty] | IEQ-19 | Places of Respite / Breakhout Space
[6 empty] | x |  | 2009-07-01 |  |  |  | IEQ-19 | Places of Respite / Breakhout Space | Correction | 1 | Places of Respite and/or Breakout Spaces located within a building do not need to be naturally ventilated but they must obtain at least 1 point from the Ventilation Rates credit in order to comply with this credit’s compliance requirements.
[7 empty] | x |  |  |  |  | IEQ-20 | Private External Space
[6 empty] | x |  | 2009-10-01 |  |  |  | IEQ-19 | Breakout Space | Technical Clarification | 1 | The requirement for the breakout space to be naturally ventilated has been removed from the credit. Instead, the projects must show that any internal breakout spaces meet the requirements for at least 1 point of IEQ-1 ‘Ventilation Rates’.
[6 empty] | x |  | 2012-08-01 |  |  |  | IEQ-19 | Breakout Space | Correction | 2 | This is a correction to the Compliance Requirements of this credit. Currently, under Ventilation on p144, the manual reads: “Where the space is mechanically ventilated, outside air is supplied at rates no less than 50% greater than the nominated within AS1668.2-1991 for 95% of nominated area; and that the HVAC system has been clearly sized to accommodate the increased outside air rates.” It should read: “Where the space is mechanically ventilated, outside air is supplied at rates no less than 50% greater than the nominated within AS1668.2-1991 for 95% of the internal breakout space; and that the HVAC system has been clearly sized to accommodate the increased outside air rates.” | 4635
[7 empty] | x | 2013-11-01 |  |  |  | IEQ-20 | Private External Space | Correction | 3 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
[7 empty] | x |  |  |  |  | IEQ-21 | Dwelling Ventilation
[7 empty] | x | 2011-01-01 |  |  |  | IEQ-21 | Dwelling Ventilation | Technical Clarification | 1 | One point can be awarded for this credit when '90% of kitchens are ventilated with dedicated and separated extract fans'. This point can be awarded, even if the other points described in the credit criteria are not awarded. | Justin: OK
[7 empty] | x | 2013-11-01 |  |  |  | IEQ-21 | Dwelling Ventilation | Correction | 2 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
x | [11 empty] | IEQ-22 | Natural Ventilation
[7 empty] | x | 2013-11-01 |  |  |  | IEQ-22 | Natural Ventilation | Correction | 1 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
x | [8 empty] | IEQ-13 |  |  |  | Air Supply Ductwork
x | [7 empty] | 2008-08-01 | IEQ-13 |  |  |  | Air Supply Ductwork | Technical Clarification | 1 | A project may claim one point where a combination of both new and existing ductwork is used, provided that the project can demonstrate that all existing ductwork was cleaned before the new ductwork was added and that all ductwork was sealed upon completion of ductwork fitout works.
x | [8 empty] | IEQ-15 |  |  |  | Indoor Plants
x | [7 empty] | 2006-09-01 | IEQ-15 |  |  |  | Indoor Plants | Technical Clarification | 1 | The plants do not have to be in individual pots, but rather be provided at the same ratio of planting surface to work settings, distributed over the NLA.
x | [7 empty] | 2007-08-01 | IEQ-15 |  |  |  | Indoor Plants | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem one plant (for one point) or two plants (for two points) per 30m2 NLA as equivalent of the current Criteria is granted provided that the plants are distributed across the NLA as per the Technical Manual: 1 point = one large or two small plant per 30m2 NLA; and 2 points = one large or two small plants per 15m2 NLA. For Green Star – Office Interiors v1 and Green Star – Office Interiors v1.1, both approaches (the one in the Technical Manual and the one outlined above) are acceptable.
x | [7 empty] | 2008-06-01 | IEQ-15 |  |  |  | Indoor Plants | Withdrawn | 3 | This clarification is beeing modified. See Clarification No.5 For more information The methodology behind the use of 200mm pots (small) & 300mm pots (large) is based on the respective surface areas of the pot itself and thereby accounts for how much soil surface area will be present. - A 200mm diameter pot = surface area of 31,450mm2 (100mm x 100mm x 3.145 = 31,450mm2) - A 300mm diameter pot = surface area of 70,762.50mm2 (150mm x 150mm x 3.145 = 70,800mm2) For example, a 900mm pot (636,900.mm2) would compare to a 300mm pot according to the correlation between the surface area of the two pots: - 636,900mm2 / 70,800mm2 = 9 pots (300mm size) Therefore nine 300mm pots would be equivalent to one 900mm pot for the purposes of this credit.
x | [7 empty] | 2008-06-01 | IEQ-15 |  |  |  | Indoor Plants | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to have the distribution of the total number of plants be across the NLA rather than on a per floor basis is granted conditionally on the project's ability to distribute the number of plants across the NLA in an equivalent manner. Projects are advised to submit case-specific CIRs.
x | [7 empty] | 2009-04-01 | IEQ-15 |  |  |  | Indoor Plants | Technical Clarification | 5 | Originally posted in June 2008 If the project is supplying pot sizes other than the sizes specified in the Technical Manual (i.e. 200mm or 300mm), the project must calculate the soil surface area to ensure what is being supplied is equivalent to the credit requirements. How to calculate soil surface area: - A 200mm diameter pot = soil surface area of 31,450mm2 (100mm x 100mm x 3.145 = 31,450mm2) - A 300mm diameter pot = soil surface area of 70,762.50mm2 (150mm x 150mm x 3.145 = 70,762.50mm2) For example, if a project is supplying a 900mm pot as an alternative to the Credit Criteria this is how you calculate the soil surface area: A 900mm pot (450mm x 450mm X 3.145 = 636,862.50mm2) would compare to a 300mm pot according to the correlation between the soil surface area of the two pots: 636,862.50mm2/ 70,762.50mm2 = 9 pots (300mm size) Therefore nine 300mm pots would be equivalent to one 900mm pot. Please note, as per the Technical Manual projects must clearly demonstrate equivalent distribution of pots across the NLA as per the Credit Criteria.
x | [7 empty] | 2009-05-01 | IEQ-15 |  |  |  | Indoor Plants | Technical Clarification | 6 | Green walls are to be calculated by measuring the soil surface area. If the soil is throughout the entire wall then the entire surface area of the wall is included. For calculating the soil surface areas please refer to Technical Clarification No.3 (see below). The project must clearly demonstrate how the Greenwall, and/or other plants in the office area are equivalently distributed across the NLA as per the Credit Criteria. If the tenancy is > 1 floor then a total of 1 green wall will not meet the aim of this credit. Please note all other requirements in the Technical Manual need to be addressed in order to meet requirements of this credit.
Note on I302: Green Building Council of Australia: Red writing is on p139 but not as much detail. Think CIR needs to be included Green Building Council of Australia: rewrite

## Ene (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Energy
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Ene-0 | Ene-0 | Ene-0 | Ene-0 | General
| x | [6 empty] | 2008-09-01 |  | Ene-0 |  |  | General | Withdrawn | 1 | See Ene-1/22
x | [7 empty] | 2008-09-01 | Ene-0 |  |  |  | General | Withdrawn | 2 | See Ene-1/16
x | x | x | x | x | x | x | x | 2013-11-01 | Ene-0 | Ene-0 | Ene-0 | Ene-0 | General | Technical Clarification | 3 | All modelling of PV systems must be carried out in line with the "Green Star - Photovoltaic Modelling Guidelines" available on the GBCA website.
x | x | x |  | x | x | x | x |  | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy / Energy Efficiency
x | x | [6 empty] | 2006-01-01 | Ene-1 | Ene-1 |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 1 | Include all systems that are noted in the submission (cogeneration, cooling towers, and solar hot water heating units).
x | x | [6 empty] | 2006-01-01 | Ene-1 | Ene-1 |  |  | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 2 | Domestic hot water is an annual amount. The overall energy use would be calculated as per the ABGR Validation Protocol and consequently include the default figure of 2kWh/m2 for domestic hot water.
| x | [6 empty] | 2007-08-01 |  | Ene-1 |  |  | Conditional Requirement / Energy Efficiency | Withdrawn | 3 | Refer to Technical Clarification No. 24 and 25 Projects may use the 2005-01 Validation Protocol.
| x | x | [5 empty] | 2007-08-01 |  | Ene-1 | Ene |  | Conditional Requirement / Energy Efficiency | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to use an approximation of the estimated thermal and visual properties of an existing façade (e.g., the U-values and shading coefficients of walls/glazing) is granted conditionally on the ability of the submission to justify that at all times, the assumptions have been conservative, i.e. described the ‘worst case scenario’. Should any project seek confirmation whether its assumptions are sufficiently conservative, CIRs justifying the assumptions must be submitted.
| x | x | [5 empty] | 2007-08-01 |  | Ene-1 | Ene |  | Conditional Requirement / Energy Efficiency | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to alter the time schedules of the ABGR Validation Protocol to reflect automatic shutdown of equipment each night is denied, because this would alter default values used by all projects, jeopardising equitable assessment and disadvantaging projects that have already completed assessment.
| x | [6 empty] | 2006-01-01 |  | Ene-1 |  |  | Conditional Requirement / Energy Efficiency | Technical Clarification | 6 | The Energy Modelling Report must reflect the documented design (for Green Star – Office Design assessment) or as-built/as-installed (for Green Star – Office As Built assessment) evidence. If a Green Star – Office Design v2 Certified Rating has been achieved and the same number of points are claimed for Green Star – Office As Built, the Certified Assessors will seek to confirm that no change to design occurred. It is recommended that in this case, the submission for Green Star – Office As Built v2 includes a confirmation from the professional responsible for the Energy Modelling Report that any changes subsequent to the issue of the reviewed Report do not alter the outcome of the modelling. In all other circumstances, the Energy Modelling Report must be reissued to reflect the as-built condition.
x | x | x | x | x | x | x | x | 2008-01-01 | Ene-1 | Ene-1 | Ene-1 | Ene | Conditional Requirement / Energy / Energy Efficiency | CIR Ruling | 7 | The Credit Interpretation Request (CIR) to deem the inclusion of the design criteria details within the base building scope of works contract equivalent to the inclusion of the same information within the Mechanical Specification is granted. However, the Certified Assessor(s) will look for a similar level of certainty as to that which they would look for within Mechanical Specifications.
| x | [6 empty] | 2008-01-01 |  | Ene-1 |  |  | Conditional Requirement / Energy Efficiency | Technical Clarification | 8 | As stated on page 3 of 6 of Ene-1 ‘Energy (Conditional Requirement)’ in Green Star – Office As Built v2, “A formal AGBR Pre-Commitment Agreement is not required to achieve this credit.”
x | x | x | x | x | x | x | x | 2008-01-01 | Ene-1 | Ene-1 | Ene-1 | Ene | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 9 | Green Star submissions are assessed purely on predictive energy modeling, not on operational performance. No period of operation is necessary; the submission for assessment can be made at any time after, and within two years of, practical completion.
| x | [6 empty] | 2008-01-01 |  | Ene-1 |  |  | Conditional Requirement / Energy Efficiency | Technical Clarification | 10 | Each variable in the Energy Modelling Report (e.g. building form, materials or air-conditioning system(s)) must be referenced consistently throughout the rest of the submission (i.e. in related credits such as IEQ-1 ‘Ventilation Rates’ or Ene-7 ‘Peak Energy Demand Reduction’) and clearly justified by the documented design (for Green Star – Office Design v2 assessment) or by the as-built evidence (for Green Star – Office As Built v2 assessment).
x | [7 empty] | 2007-01-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 11 | This ruling has been withdrawn as of 01-Nov-13. Whatever the occupant density, the default of one occupant per 18 sq. m. must be used.
x | [7 empty] | 2007-12-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 12 | Equipment in non-office spaces can be excluded from the assessment provided that it meets the requirements of the ABGR Validation Protocol for Tenancy Energy Estimation such as separate metering (refer to clause 4.4.2).
x | [7 empty] | 2006-09-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | CIR Ruling | 13 | The following clarification has been withdrawn. It has been replaced by TC No. 31. (Originally Posted on Sep 06) Projects may use actual values for the peripheral loads in the ABGR Validation Protocol for Tenancies formula if they demonstrate (via a schedule with supporting documentation) that their peripheral loads are less than the normalized 80 w/person. The rest of the values used for the estimation must be as per the current AGBR Validation Protocol for Tenancies. In the Validation Protocol, the default allowance for peripherals of 80W per PC should be subtracted from the default allowances for standard office equipment. These values are stated in the Ene-1 Table tab. See the Ene-1 Table No.1 for more information
x | [7 empty] | 2006-09-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | CIR Ruling | 13 | The allowance for peripheral loads includes standard office equipment (if applicable): - server/computer rooms (a conservative default is 1,000W/m2 (excluding HVAC); it is acceptable to give actual value from the previous site on a per-square-meter basis) - printers - photocopiers - fax machines - scanners - PC peripherals - task lighting - tea room facilities (other than refrigerators, freezers, refrigerated drink dispensers and hot water/chilled water units, which are addressed separately - see the Validation Protocol). Therefore, values for the same equipment must be included in the calculations of actual peripheral loads.
x | [7 empty] | 2007-08-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 14 | According to the ABGR Validation Protocol, the actual number of computers must be used, whether it is higher or lower than one unit per workstation. You may calculate this on the number of CPUs (i.e. disregard multiple screens per CPU). Projects can use the version of the ABGR Validation Protocols stipulated in the Technical Manuals or subsequent versions.
x | [7 empty] | 2006-06-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 15 | Withrawn as of the 01-Jul-12. Replaced by ruling #39. For the purposes of energy modeling in accordance with the ABGR Validation Protocol, fitouts in Victoria, Queensland and South Australia may specify New South Wales as their location.
x | [7 empty] | 2006-06-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 16 | See Ene-1/9
x | [7 empty] | 2007-08-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | CIR Ruling | 17 | The Credit Interpretation Request (CIR) to use an approximation of the estimated thermal and visual properties of an existing façade (e.g., the U-values and shading coefficients of walls/glazing) is granted conditionally on the ability of the submission to justify that at all times, the assumptions have been conservative, i.e. described the 'worst case scenario'. Should any project seek confirmation whether its assumptions are sufficiently conservative, CIRs justifying the assumptions must be submitted.
x | [7 empty] | 2007-08-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 18 | See Ene-1/4
x | [7 empty] | 2007-12-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | CIR Ruling | 19 | The Credit Interpretation Request (CIR) to attribute the energy generated by the tenancy on site towards its reduction in greenhouse emissions is granted conditionally on the following points being clearly demonstrated in the submission: - The power generated by the tenancy (wherever the generation occurs in the building) is recirculated directly to the substation power board with contractual metering between the building owner and the tenant; - A single-line electrical diagram demonstrating that the tenant loads and the co-generation connection; - Evidence that the energy subtraction is factored in the ABGR energy modelling as per Green Star – Office Interiors v1.1 Ene-1 requirements; and - Evidence that the co-generation supply will be attributed wholly to the tenant's electrical bill (e.g. that the tenant has not installed authority sub-meters).
x | [7 empty] | 2007-08-01 | Ene-1 |  |  |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 20 | See Ene-1/5
| x | [6 empty] | 2008-09-01 |  | Ene-0 |  |  | Conditional Requirement / Energy Efficiency | Technical Clarification | 21 | The ‘12w/m2'’ figure for tenancy lighting density loads mentioned in Chapter Five of the ABGR Validation Protocol for Computer Simulations and the NABERS Energy Guide to Building Energy Estimation is applicable to “shell and core buildings” only. All other buildings must use their design loads + 1w/m2, as stated in the same document.
[8 empty] | 2008-09-01 |  |  |  | Ene | General | Technical Clarification | M1 | It is considered standard practice to have lighting and AC controls within the dwelling. Therefore, standard operating hours as outlined in the Energy Calculator guide must be used. Projects may not alter these profiles.
[8 empty] | 2008-09-01 |  |  |  | Ene | General | Technical Clarification | M2 | The operating profiles of kitchen and bathroom exhausts must be used, even if, the actual operation is known. This will ensure that the all projects are assessed fairly against the benchmarks.
[8 empty] | 2008-09-01 |  |  |  | Ene | General | Technical Clarification | M3 | Emergency lighting systems within the building and all internal carparks can be excluded from the energy modelling for this credit.
[8 empty] | 2008-09-01 |  |  |  | Ene | General | Technical Clarification | M4 | The gas consumption for co-generation must be allocated to the HVAC gas requirements in the energy calculator.
[8 empty] | 2008-09-01 |  |  |  | Ene | General | Technical Clarification | M5 | The gas consumption for the swimming pool must be allovated to the domestic hot water gas consumption cell.
[8 empty] | 2008-10-01 |  |  |  | Ene | General | Technical Clarification | M6 | The energy calculator guide states that if occupancy sensors or timeclocks are installed in common areas, then "the appropriate lighting profile" must be followed. The profiles given are the hours of operation included in Appendix D. Lighting controls are awarded in Ene-4.
[8 empty] | 2008-10-01 |  |  |  | Ene | General | Technical Clarification | M7 | The amenities, internal and external carpark lighting hours of use are calculated at 12hr/day. This assumes 8am-8pm operation for amenities and sundown to sunup for car parks. The foyers, hallways, corridors and back of house are calculated at 8 hr/day. This assumes an 8 hour working day for back of house areas and an average 8 hr/day for foyers etc. This was put to the TWG for review and comment and was approved. These are to be used for all calculations. So long as all projects use the same profile and the benchmark is based on this profile, projects will compared equitably and the calculator will awarding low power density design. ENE-4 awards points for lighting controls.
[8 empty] | 2008-10-01 |  |  |  | Ene | General | Technical Clarification | M8 | Guidelines for calculating the air conditioning load of the common areas for the pilot tool has not been provided. For purposes of the pilot, the calculations shall be made by a suitably qualified professional and all assumptions must be well justified.
[8 empty] | 2008-10-01 |  |  |  | Ene | Conditional Requirement | Technical Clarification | M1 | The following documentation must be submitted for this credit: + Thermal Performance Modelling Report containing: - Summary table of all units’ NatHERS (second generation) ratings (i.e. produced using either FirstRate5, BERS Professional or AccuRate); - Details of all inputs in the models; - Calculation of the building average score (used for Ene-1); and + NatHERS certificates for the building.
| x | x | [5 empty] | 2008-12-01 |  | Ene-1 | Ene | Ene | Conditional Requirement / Energy Efficiency | Technical Clarification | 22 | A stacker system will use energy not previously envisioned by the ABGR validation protocol. Therefore, to ensure a consistent assessment across all Credits, the system’s energy consumption must be considered in ENE-1 & 2. Energy consumption is to be calculated on 1 usage (a single raise and lower) per business day for every stacker.
| x | x | [5 empty] | 2008-12-01 |  | Ene-1 | Ene | Ene | Conditional Requirement / Energy Efficiency | CIR Ruling | 23 | The Credit Interpretation Request (CIR) to deem these Credits ‘Not Applicable’, as the project is being delivered as a shell and core project, is denied. This change would alter default values used by all projects, jeopardising equitable assessment and disadvantaging projects that have already obtained their rating.
x | x | x | [5 empty] | 2008-12-01 | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy Efficiency | Technical Clarification | 24 | Projects can use the version of the ABGR Validation Protocol stipulated in the Technical Manuals or the version current at the time of Registration, or any version that officially supersedes it (including the NABERS Energy Guide for Building Energy Estimation). Projects must clearly state which version of the Validation Protocol is being used in their submission.
x | x | x | x | x | x | x | x | 2008-12-01 | Ene-1 |  |  |  | Conditional Requirement / Energy Efficiency | Technical Clarification | 25 | This clarification has been withdrawn. It is duplicated in TC 9 in this credit. The Ene, Ene-1, and Ene-2 credits within a Green Star submission are assessed purely on predictive energy modeling, not on operational performance. No period of operation is necessary; the submission for assessment can be made at any time after, and within two years of, practical completion.
|  | x | [5 empty] | 2009-03-01 |  |  | Ene |  | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 26 | Green Star – Office v3: Approach to Greenhouse Gas Emissions There are two credits within Green Star – Office Design and Office As Built version 3 (v3) rating tools that directly target greenhouse gas emissions. These credits are the Ene-Conditional Requirement (Ene-CR) and Ene-1 ‘Greenhouse Gas Emissions’ (Ene-1). The key aim of Ene-CR and Ene-1 within Green Star is to reward reductions in the greenhouse gas emissions associated with buildings. To demonstrate compliance with these credits energy modelling is currently required. In Green Star – Office v3 the credit Ene-CR must be achieved for the project to be eligible for assessment and certification, whilst Ene-1 rewards predicted ‘net zero greenhouse gas emissions in operation’ with the maximum 20 points. Compliance with Ene-CR and Ene-1 can be achieved through one of the two methods described in the GHG Tab in this spreadsheet, or found at: http://www.gbca.org.au/uploads/174/1710/Green%20Star%20Fact%20Sheet%20-%20Approach%20to%20GHG%20Emissions%20in%20Energy.pdf
x | x | x | [5 empty] | 2009-05-01 | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 27 | Additional compliance path available for projects that have signed a NABERS Commitment Agreement: Projects that have signed a NABERS Commitment Agreement are automatically eligible for points in Green Star – Office and Green Star – Office Interiors; no further modelling is required. - For projects seeking points equivalent to a NABERS 5 star rating or less, only the commitment agreement is required. - For projects seeking points equivalent to more than a NABERS 5 star rating, the commitment agreement and a statement or design review document from the independent NABERS Design Review Panel stating the simulated kg CO2/m2 is required.
|  |  |  | x |  |  |  | 2009-07-01 | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy / Energy Efficiency | Technical Clarification | 28 | Addressing Server Rooms As per the Green Star - Education Energy Calculator Guide, the energy requirement of process loads, such as equipment within a school (desktop computers, science equipment, kilns etc…) or server rooms, does not need to be included. The load profile for “Dry Labs” as seen in the Energy Calculator Guide must be used when assigning a profile to server rooms.
|  |  |  | x |  |  |  | 2009-07-01 | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 29 | This clarification has been withdrawn. See Technical Clarification No. 30 for more information. (Originally posted on Dec-07) External Lighting External lighting, such as the that used for car park, or general lighting, is required to be included within Green Star, with the exception of security lighting as required by the BCA. The energy consumed by carpark lighting must included in the carpark field within the energy calculator. Any additional external lighting such as lighting to footpaths, lighting to the building, goes into the “Other” field, within the “Extras” section of the calculator. A lighting schedule of 12 hours is required to be used for all external lighting. If a project designs a system with lighting control systems, they must submit a CIR if they wish to alter the lighting schedule for external lighting (as seen in Table 29, Green Star - Education v1 Energy Calculator Guide, January 2010).
|  |  |  | x |  |  |  | 2011-01-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | Correction | 30 | External Lighting The energy consumed by carpark lighting must be included in the carpark field of the energy calculator. Additional external lighting such as lighting of footpaths or the building facade, should not be included in the energy consumption calculations. They are addressed by a different credit in this rating tool. A CIR must be submitted for any carpark lighting system with automated controls, if it results in a different 'Lighting Energy Consumption Profile' to the one listed in the Energy Calculator Guide.
x | [7 empty] | 2011-01-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | CIR Ruling | 31 | The following clarification has been amended to describe when this clarification can be used. For projects using the ABGR Validation Protocol for Tenancy Energy Estimation 2005: Calculation Method One: Default allowance for standard office equipment must be as per the current AGBR Validation Protocol for Tenancies. Default allowance for peripherals of 80W per PC should be subtracted from the default allowances for standard office equipment. See the Ene-1 Table No.1 included in this spreadsheet, for more information. Calculation Method Two: Where actual peripheral loads are known to be less than the normalized 80 w/person, projects may use those actual values in these calculations. The peripheral loads must be verified by a schedule with supporting documentation. The peripheral load calculations must include the following where they occur in the project: -printers; photocopiers; fax machines; scanners; PC peripherals; task lighting; tea room facilities. The peripheral load calculations must exclude the following: -refrigerators; freezers; refrigerated drink dispensers; hot water/chilled water units. (These are addressed separately in the validation protocol.) Any other values used for the estimation must be as per the current AGBR Validation Protocol for Tenancies. See the Ene-1 Table No.1 included in this spreadsheet, for more information.
| x | [6 empty] | 2006-01-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | Technical Clarification | 32 | As clarifications for the Energy Conditional Requirement, 'Greenhouse Gas Emissions', and 'Energy Improvements' are identical. We have moved all clarifications to one combined section. This clarification used to be listed as Ene-2/1 (for Office v2 and Office Interiors) and Ene-1/1 (for all other tools). Correction 35 does not reward projects for having car parks. It is intended to ensure fair treatment for projects whose ABGR score has been lowered because their car parking spaces are on grade or internal. The environmental impact of car parks is addressed under Transport.
| x | x | x | x | x |  |  | 2008-12-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | Technical Clarification | 33 | As clarifications for the Energy Conditional Requirement, 'Greenhouse Gas Emissions', and 'Energy Improvements' are identical. We have moved all clarifications to one combined section. This clarification used to be listed as Ene-2/2 (for Office v2 and Office Interiors) and Ene-1/2 (for all other tools). As-Built projects that have been previously awarded points for these credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credit (i.e. same shape floor plan, same glazing propoerties and floor-to-ceiling height) can submit a letter from the relevant consultant in place of an as-built model (the as-built drawings must still be provided). The letter must describe the extent of any changes and state the maximum impact they may have on the building performance if it were remodelled. In this case the number of points achieved in the Design rating will automatically be awarded. Please note: Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Modelling must account for worse case scenario; please see the assumptions clarification for more information.
x | x | x | x | x | x | x | x | 2008-12-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | Technical Clarification | 34 | As clarifications for the Energy Conditional Requirement, 'Greenhouse Gas Emissions', and 'Energy Improvements' are identical. We have moved all clarifications to one combined section. This clarification used to be listed as Ene-2/3 (for Office v2 and Office Interiors) and Ene-1/3 (for all other tools). Modelling software used for Ene-CR and Ene-1 will must be reported on by an independent assessor. This report must confirm that the software complies with BESTEST and/or ASHRAE standard 140-2004. This report must have the capacity to accept all the inputs/conditions outlined in the Technical Manual e.g. weather data files.
| x | [6 empty] | 2009-05-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Conditional Requirement / Energy / Energy Efficiency/ Greenhouse Gas Emmissions / Energy Improvements | Correction | 35 | As clarifications for the Energy Conditional Requirement, 'Greenhouse Gas Emissions', and 'Energy Improvements' are identical. We have moved all clarifications to one combined section. This clarification used to be listed as Ene-2/6 (for Office v2 and Office Interiors) and Ene-1/6 (for all other tools). Projects cannot claim the car parking adjusment point for this credit, where their specific parking requirements do not meet the criteria described in the Technical Manual. The car park correction does not reward projects for having car parks. It is purely intended to compensate projects whose NABERS Energy (previously ABGR) score was lower because their car parks are within the building shell (as opposed to being external). This allows projects to be compared on an equitable basis. The aim of the additional points for provision of car parking are intended to compensate projects with large car parking numbers provided within the building shell, not for the energy consumed by additional services provided in a basement car park. The fact that a building has basement facilities instead of car parks is not justification enough to claim these points.
[7 empty] | x | 2011-01-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Greenhouse Gas Emissions | Credit Intepretation Request | 36 | Dynamic energy modelling of typical and identical floors is acceptable provided the following parameters are the same for all typical levels: Apartment type/layout Air-conditioning layout and arrangement External shading devices Impacts from surrounding buildings The following supporting documentation must be provided with the submission: A table summarising the typical floors to be included in dynamic energy simulations Marked-up schematics of the development showing how typical floors have been grouped.
|  | x |  | x | x | x | x | 2012-08-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Greenhouse Gas Emissions | Technical Clarification | 37 | For Design projects where thermal properties of constructions have not yet been specified, project teams may assume NCC Deemed-to-satisfy thermal performance. In these situations the project team may replace "extract(s) from the specification(s)" with the following documentation to demonstrate the thermal properties of new material constructions used in the model: A section within the Modeling Report which lists all material types which form the building envelope and nominates whether: 1. The material constructions and properties have been specified (in which case a specification will still be required for these materiasl); or 2. The NCC deemed-to-satisfy performance has been assumed. - Where material constructions and properties have been specified and shown on drawings, the project team must provide calculations to demonstrate the thermal properties of the constructions using industry standard values; - Where the NCC deemed-to-satisfy performance has been assumed, the specification must require adherence to the deem-to-satisfy requirements of NCC Section J for the year in which the project obtained DA approval. The project team must also demonstrate that the thermal properties used are consistent across all other modelling credits within the submission.
x | [7 empty] | 2012-08-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Greenhouse Gas Emissions | Technical Clarification | 38 | This is a clarification of the documentation requirements for this credit. With regards to providing evidence of the type and quantity of light fittings to be used within the tenancy, please provide: - As Built drawings that detail installed luminaire fittings and switch types and locations. This replaces the requirement for: - The lighting specification showing fittings and controls.
x | [7 empty] | 2012-08-01 | Ene-1/Ene-2 | Ene-1/Ene-2 | Ene-Con/Ene-1 | Ene-Con/Ene-1 | Greenhouse Gas Emissions | Technical Clarification | 39 | For the purposes of energy modeling in accordance with the NABERS Energy Guide to Tenancy Energy Estimation, fitouts in all states and territories may specify New South Wales as their location.
x | x | x | x | x | x | x | x |  | Ene-2 | Ene-2 | Ene-1 | Ene-1 | Greenhouse Gas Emmissions / Energy Improvements
| x | [6 empty] | 2011-01-01 |  | Ene-2 |  |  | Greenhouse Gas Emmissions / Energy Improvements | MOVED | 1 | This TC has been MOVED to the 'Conditional Requirement / Energy / Energy Efficiency' section in Feb 2010. The car park correction does not reward projects for having car parks. It is purely intended to compensate projects whose ABGR score was lower because their car parks are on grade or within the building shell (as opposed to being external). As a result, all projects can be compared on an equitable basis. The environmental impact of car parks is addressed under Transport.
| x | x | x | x | x |  | x | 2011-01-01 | Ene-1 | Ene-2 | Ene-1 | Ene-1 | Greenhouse Gas Emmissions / Energy Improvements | MOVED | 2 | This TC has been MOVED to the 'Conditional Requirement / Energy / Energy Efficiency' section in Feb 2010. As-Built projects that have been previously awarded points for these credits as part of a Green Star - Office Design rating, and that have not been modified from the previous submission so as to affect the outcome of such credit (i.e. same shape floor plan, same glazing propoerties and floor-to-ceiling height) can submit a letter from the relevant consultant in place of an as-built model (the as-built drawings must still be provided). The letter must describe the extent of any changes and state the maximum impact they may have on the building performance if it were remodelled. In this case the number of points achieved in the Design rating will automatically be awarded. Please note: Assessor(s) will cross-reference with other related credits and reserve the right to request resubmission of evidence if inputs appear to differ. Modelling must account for worse case scenario; please see the assumptions clarification for more information.
x | x | x | x | x | x | x | x | 2011-01-01 | Ene-1 | Ene-2 | Ene-1 | Ene-1 | Greenhouse Gas Emmissions / Energy Improvements | MOVED | 3 | This TC has been MOVED to the 'Conditional Requirement / Energy / Energy Efficiency' section in Feb 2010. Modelling software used for Ene-CR and Ene-1 will need to be independently verified to comply with BESTEST and/or ASHRAE standard 140-2004 and to have the capacity to accept all the inputs/conditions outlined in the Technical Manual (such as a weather file/data).
|  | x | [5 empty] | 2011-01-01 |  |  | Ene |  | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 4 | This TC has been WITHDRAWN. It is IDENTICAL to TC 26 in the 'Conditional Requirement / Energy / Energy Efficiency' section.) Green Star – Office v3: Approach to Greenhouse Gas Emissions There are two credits within Green Star – Office Design and Office As Built version 3 (v3) rating tools that directly target greenhouse gas emissions. These credits are the Ene-Conditional Requirement (Ene-CR) and Ene-1 ‘Greenhouse Gas Emissions’ (Ene-1). The key aim of Ene-CR and Ene-1 within Green Star is to reward reductions in the greenhouse gas emissions associated with buildings. To demonstrate compliance with these credits energy modelling is currently required. In Green Star – Office v3 the credit Ene-CR must be achieved for the project to be eligible for assessment and certification, whilst Ene-1 rewards predicted ‘net zero greenhouse gas emissions in operation’ with the maximum 20 points. Compliance with Ene-CR and Ene-1 can be achieved through one of the two methods described in the GHG Tab in this spreadsheet, or found at: http://www.gbca.org.au/uploads/174/1710/Green%20Star%20Fact%20Sheet%20-%20Approach%20to%20GHG%20Emissions%20in%20Energy.pdf
x | x | x | [5 empty] | 2011-01-01 | Ene-1 | Ene-1 | Ene | Ene | Conditional Requirement / Energy / Energy Efficiency | Withdrawn | 5 | This TC has been WITHDRAWN. It is IDENTICAL to TC 27 in the 'Conditional Requirement / Energy / Energy Efficiency' section.) Additional compliance path available for projects that have signed a NABERS Commitment Agreement: Projects that have signed a NABERS Commitment Agreement are automatically eligible for points in Green Star – Office and Green Star – Office Interiors; no further modelling is required. - For projects seeking points equivalent to a NABERS 5 star rating or less, only the commitment agreement is required. - For projects seeking points equivalent to more than a NABERS 5 star rating, the commitment agreement and a statement or design review document from the independent NABERS Design Review Panel stating the simulated kg CO2/m2 is required.
x | x | [6 empty] | 2011-01-01 | Ene-2 | Ene-2 | Ene-1 | Ene-1 | Greenhouse Gas Emmissions / Energy Improvements | MOVED | 6 | This TC has been MOVED to the 'Conditional Requirement / Energy / Energy Efficiency' section. Projects cannot claim the car parking adjusment point for this credit, where their specific parking requirements do not meet the criteria laid out in the Technical manual. The car park correction does not reward projects for having car parks. It is purely intended to compensate projects whose NABERS Energy (previously ABGR) score was lower because their car parks are within the building shell (as opposed to being external). This allows projects to be compared on an equitable basis. The aim of the additional points for provision of car parking are intended to compensate projects with large car parking numbers provided within the building shell, not for the energy consumed by additional services provided in a basement car park. The fact that a building has basement facilities instead of car parks is not justification enough to claim these points.
x | x | x | x | x | x | x | x |  | Ene-3 | Ene-3 | Ene-2 | Ene-2 | Energy Sub-metering / Electrical Sub-metering
| x | [6 empty] | 2007-01-01 |  | Ene-3 |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 1 | Whenever lifts, individually or collectively, carry an energy use greater than 100kVa, they must be sub metered. If individually, lifts carry an energy use under 100kVa, they can be sub metered individually or as a group. If individually, they carry an energy use greater than 100kVa, they must be sub metered separately unless they are monitored by an intelligent control system.
| x | [6 empty] | 2008-10-01 |  | Ene-3 |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 2 | While this is not a current requirement of the Technical Manual, to assist the Certified Assessors in assessing this credit and avoid possible questions, projects are advised to submit a schedule of all equipment in excess of 100Kva, or identify the kVA of each switchboard (on the single line diagram). This can be included in the drawings provided by the project team or in a separate document.
x | [7 empty] | 2006-09-01 | Ene-3 | Ene-3 |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 3 | Lighting and small power must be sub-metered separately, i.e. one meter for lighting and one meter for small power.
x | [7 empty] | 2008-07-01 | Ene-3 |  |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 4 | The 25kVA applies to individual items OR systems. Systems that are less than 25kVA CAN be grouped together under one sub meter if they are of: - Identical use, and - A substantive energy use. For example, where there are a number of communications rooms each less than 25kVA on each floor, they can be metered together to form a substantive use larger than 25kVA. It is important to note that the aim of this credit is to facilitate energy monitoring of substantive energy uses; Certified Assessor(s) will be looking to ensure that the sub-metering can provide useful information. So, while grouping a number of communication rooms would meet this criterion, grouping a large number of computers spread throughout the building would not.
x | [7 empty] | 2008-08-01 | Ene-3 |  |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 4 | The following clarification is an expansion of the above: The following systems that can be grouped together to achieve the Credit Criteria are: - Computer Server Rooms; - Computer Rooms Air Conditioning - Communications Room; - Meeting Rooms; - Supplementary Air Conditioning Systems; - Print Rooms. Please note that each of these uses must be sub-metered individually whenever it is at or above 25kVA.
x | [7 empty] | 2008-09-01 | Ene-3 |  |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 5 | The Credit Interpretation Request (CIR) to exclude the area and energy use of a commercial kitchen operated by an external catering company from the ABGR (now NABERS Energy) calculations is granted conditionally. The project may either: - Exclude the energy and area of the kitchen if the energy use of this kitchen is clearly sub-metered and each sub-meter meets the Compliance Requirements of Ene-3 ‘Electrical Sub-metering’; OR - Include the energy and area of the kitchen in the modelling. Regardless of which option is chosen, the project must justify all assumptions. Please note: This ruling does not exclude this area from assessment in any other credits within the Green Star – Office Interiors v1.1 rating tool. Please note that this Technical Clarification/CIR Ruling applies to the "ABGR Validation Protocol for Tenancy Energy Estimation" only.
x | x | x | [5 empty] | 2008-10-01 | Ene-3 | Ene-3 | Ene-2 |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 6 | While this is not a current requirement of the Technical Manual, to assist the Certified Assessors in assessing this credit and avoid possible questions, projects are advised to submit a schedule of all equipment in excess of 25Kva (for interiors) or 100KvA (for all base building tools), or identify the kVA of each switchboard (on the single line diagram). This can be included in the drawings provided by the project team or in a separate document.
x | x | [6 empty] | 2008-12-01 | Ene-3 | Ene-3 |  |  | Energy Submetering / Electrical Sub-metering | Technical Clarification | 7 | For clarity and ease of assessment of this Credit, it is recommended that projects submit a single line diagram to indicate electrical loads (for all building services) and metering provisions.
x | [7 empty] | 2009-07-01 | Ene-3 |  |  |  | Energy Sub-metering / Electrical Sub-metering | Technical Clarification | 8 | If a project does not install any electrical sub-metering, even if there are no substantive uses over 100kVA, then this credit cannot be claimed. This credit can only be claimed when sub-meters have been provided by the base building, or as installed by the tenant.
x | x | x | x | x | x | x | x | 2011-01-01 | Ene-3 | Ene-3 | Ene-2 | Ene-2 | Energy Sub-metering / Electrical Sub-metering | Technical Clarification | 9 | On site energy generation systems must be sub-metered.
x | [7 empty] | 2011-01-01 | Ene-3 |  |  |  | Energy Sub-metering | Technical Clarification | 10 | The Additional Point can be claimed as Not Applicable without any of the first points being claimed. It must be demonstrated that there are no energy uses greater than 25 kVA.
x | x | x | x | x | x | x | x |  | Ene-3 | Ene-4 | Ene-2 | Ene-2 | Energy Sub-metering / Tenancy Sub-metering
x | x | [6 empty] | 2008-12-01 | Ene-3 | Ene-4 |  |  | Energy Sub-metering / Tenancy Sub-metering | Technical Clarification | 1 | For clarity and ease of assessment of this Credit, it is recommended that projects submit a single line diagram to indicate electrical loads (for all building services) and metering provisions.
|  |  | x |  |  |  |  | 2009-03-01 |  |  |  | Ene-2 | Energy Sub-metering | Correction | 2 | In both documentation requirements for Design and As Built ratings for this credit, the Short Report states: 'Where the additional point is claimed, describing how sub-metering is provided separately for lighting and separately for power for each floor or tenancy, whichever is smaller, and the effective mechanism for monitoring energy consumption data.' It should read: 'Where the additional point is claimed, describing how sub-metering is provided separately for each tenancy, and the effective mechanism for monitoring energy consumption data.'
| x | x | [7 empty] | Ene-5 | Ene-3 | Ene-5 | Lighting Power Density
| x | [6 empty] | 2006-01-01 |  | Ene-5 |  |  | Lighting Power Density / Office Lighting Power Density | Technical Clarification | 1 | To claim this credit, full lighting capacity (not dimmed) must be included in calculations. Green Star assesses the capacity of building's attributes to reduce its environmental impact. Any design that allows for greater luminance levels does not meet the aim of this credit because tenant operations and/or behaviour can reverse the effort of the commissioning and prevent utilisation of the full capacity of the design.
| x | x | [5 empty] | 2008-04-01 |  | Ene-5 | Ene-3 |  | Lighting Power Density / Office Lighting Power Density | Technical Clarification | 2 | Where the values for the surface reflectance are unknown, the values for modelling these credits must be in accordance with the values stated in the Compliance Requirements section of IEQ-4.
|  | x | [5 empty] | 2011-01-01 | Ene-0 | Ene-5 | Ene-3 | Ene-5 | Lighting Power Density | Correction | 3 | The Credit Criteria for the Green Star - Office V3 rating tool awards points as follows: 1 point for 2.5 W/m2 per 100 lux 2 points for 2 W/m2 per 100 lux and 3 points for 1.5 W/m2 per 100 lux The example given in the Technical Manual for this credit is inconsistent with the credit criteria for Green Star - Office V3 The example shows an average of 2.8W/m2 per 100 lux resulting in 1 point. It is not correct and should be disregarded.
|  | x | [5 empty] | 2009-03-01 |  | Ene-5 | Ene-3 | Ene-5 | Lighting Power Density | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from specification(s) Furthermore, the following documentation is being modified. * Tender Reflected Ceiling Plan or Tender Lighting Plan indicating the location and area of each typical lighting layout, the luminaires used, the types of lamps used for each fitting, the ballasts and control systems. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | [5 empty] | 2009-03-01 |  | Ene-5 | Ene-3 | Ene-5 | Lighting Power Density | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation(s) from the supplier(s) All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x |  | x | x | x |  |  | Ene-4 | Ene-6 | Ene-4 | Ene-4 | Lighting Zoning / Office Lighting Zoning
x | x | x | [5 empty] | 2007-12-01 | Ene-4 | Ene-6 | Ene-4 |  | Lighting Zoning / Office Lighting Zoning | Technical Clarification | 1 | Controlling alternate rows by separate switches in a lighting zone that exceeds 100m2 does not meet the intent of the credit to minimise energy consumption necessary for performing a task in a specific area, as it is likely that both switches will be on simultaneously to provide the desired lighting level.
| x | [6 empty] | 2007-08-01 |  | Ene-6 |  |  | Lighting Zoning / Office Lighting Zoning | Withdrawn | 2 | Motion occupancy sensors are treated the same way as switching, but they must be automated with a manual override, and connected to a system that will automatically turn off all lighting after hours.
x | x | x | [5 empty] | 2006-09-01 | Ene-4 | Ene-6 | Ene-4 |  | Lighting Zoning / Office Lighting Zoning | Technical Clarification | 3 | An 'individually addressable lighting system' is one in which lighting fixtures can be readdressed/regrouped without rewiring.
x | [7 empty] | 2007-08-01 | Ene-4 |  |  |  | Lighting Zoning / Office Lighting Zoning | Withdrawn | 4 | Previously Ene-4 Technical Clarification No. 2 As there can be a significant difference in the load between lighting and power, it has been clarified that tenancy lighting and power must be sub-metered separately from each other.
x | x | x |  | x | x | x |  | 2009-02-01 | Ene-4 | Ene-6 | Ene-4 | Ene-4 | Lighting Zoning / Office Lighting Zoning | Withdrawn | 5 | Withdrawn on 01/11/2013. Please refer to Technical Clarification No. 10 Where projects have installed an addressable lighting control system, the following must be shown in the documentation provided: - Provide drawings with all soft switches highlighted and identified and ensure an electrical services legend that identifies the various symbols on the drawings relate to is included. (Soft switch – an addressable switching mechanism such as light level detectors, motion detectors and light switches which are connected to an addressable lighting control system). - Provide a statement from the electrical or lighting designers and contractor that no zone exceeds 100m2. - Ensure the drawings provided represent each typical floor/lighting layout (i.e. the drawing must be a typical lighting layout); where lighting layouts are different on each floor, then drawings for each floor must be provided.
|  |  |  | x |  |  |  | 2010-03-01 |  |  |  | Ene-4 | Lighting Zoning / Office Lighting Zoning | Correction | 6 | As part of the continuous improvement of Green Star - Education v1, the GBCA undertook a review of Ene-4 'Lighting Zoning'. This revised credit is the result of such work. As of March 19th, 2010 this revised version of the credit replaces published version in the Green Star - Education v1 Technical Manual. The revised version differs as follows: - The requirement for automatic lighting controls has been removed from the Credit Criteria. - It is now required that individually switched lighting zones do not exceed 100m2 for 95% of the nominated area. - The nominated area has been revised to exclude external covered areas, auditoriums, theatres, swimming pools and sports halls. Projects that register after March 19th, 2010 must use the revised version of the credit. Projects registered prior to this date have the option of continuing with the credit found in the Technical Manual, or using this revised version. Where projects registered prior to this date choose to use the revised version, this must be indicated on the cover page of this credit in their submission. The new credit can be downloaded by following this link, or by clicking on this cell: http://www.gbca.org.au/green-star/green-star-education-v1-ene-4-lighting-zoning/2856.htm
|  | x | [5 empty] | 2011-01-01 |  |  | Ene-4 |  | Lighting Zoning | Technical Clarification | 7 | For the purpose of Green Star assessment under the Ene-4 credit, an individually addressable lighting system is defined as a system where each light fitting can be addressed, controlled, and dimmed individually. Furthermore, it must have the ability to be controlled in a group, and also be re-addressable to suit future churn or modifications to fitout.
|  | x | [5 empty] | 2011-01-01 |  |  | Ene-4 |  | Lighting Zoning | Technical Clarification | 8 | A motion sensor lighting system can be classified as a ‘switch’ provided that the aim of the credit is still met. If used, motion sensor timer must be set as follows: - For meeting rooms, the maximum timer setting must be set to switch off after 20 minutes of inactivity - For open plan areas, the maximum timer setting must be set to switch off after one 1 hour of inactivity.
|  | x | [5 empty] | 2011-01-01 |  |  | Ene-4 |  | Lighting Zoning | Technical Clarification | 9 | Where motion sensors are present, the following additional information must be included in your submission in addition to what is required in the Technical Manual: For a Design rating: - A short report that shows how lights are switched (including proposed timings of each functional area), listing all zones and their areas, and demonstrating that no zone exceeds 100m2. - Extract(s) from the specification that describes the switching strategy from the short report. - Tender drawings demonstrating the zones and location of sensors. For an As Built rating: - A short report that shows how lights are switched (including proposed timings of each functional area), listing all zones and their areas, and demonstrating that no zone exceeds 100m2. - As Built drawings demonstrating the zones and location of sensors. - Extract(s) from the Commissioning Report showing that the sensors have been tested, work as installed, with the sensor timer accurately calibrated.
X | X | X |  | X | X | X |  | 2013-11-01 | Ene-4 | Ene-6 | Ene-4 | Ene-4 | Lighting Zoning | Technical Clarification | 10 | Where projects have installed an addressable lighting control system, the following must be shown in the documentation provided: - Drawings with all soft switches identified and highlighted, including an electrical services legend identifying symbols used. (Soft switch - an addressable switching mechanism such as a light level detector, motion detector or light switch, which is connected to an addressable lighting control system). - A statement from the electrical or lighting designers or contractor that no zone exceeds 100m2 for 95% of the tenancy. - Ensure the drawings provided represent each typical floor or lighting layout; and where lighting layouts differ between floors, drawings for each floor must be provided.
|  | x |  | x | x | x |  | 2009-03-01 | Ene-4 | Ene-6 | Ene-4 | Ene-4 | Lighting Zoning / Office Lighting Zoning | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Tender schematic electrical drawings * Tender single-line diagram * Tender floor plan drawings Projects must submit the following documentation instead: * Tender Lighting plan identifying the control zone and the luminaire and switch locations. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x |  | x | x | x |  | 2009-03-01 | Ene-4 | Ene-6 | Ene-4 | Ene-4 | Lighting Zoning / Office Lighting Zoning | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * As-built electrical drawings * Confirmation from the contractor * Extract(s) from the specification(s) * As-built floor plan drawing(s) Projects must submit the following documentation instead: * As Built Lighting plan identifying the control zone and the luminaire and switch locations. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x |  |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction
| x | [6 empty] | 2006-01-01 |  | Ene-7 |  |  | Peak Energy Demand Reduction | Technical Clarification | 1 | Unless they are designed and integrated into the base building for the purpose of peak energy demand reduction and can be initiated and turned off without causing a blackout, diesel or other types of stand-by generators do not qualify for this credit.
| x | [6 empty] | 2007-08-01 |  | Ene-7 |  |  | Peak Energy Demand Reduction | Technical Clarification | 2 | Any peak energy demand reduction must be reflected in the evidence for Ene-7 'Peak Energy Demand Reduction', the Certified Assessor(s) will seek to verify that it has been accommodated in commissioning credits for all relevant services, such as Man-2 'Commissioning: Commissioning Clauses', Man-3 'Commissioning: Building Tuning', Man-4 'Commissioning: Independent Commissioning Agent', Man-5 'Building Users' Guide', Ene-2 'Energy Improvement' and IEQ-12 'Internal Noise Levels', whenever claimed. Consistency with the amended design will be required whenever the above credits are to contribute to the project's final rating, even if they have been awarded. This may require that certain evidence be resubmitted for previously awarded credits to demonstrate such consistency.
| x | x | x | x | x | x | x | 2007-08-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | Withdrawn | 3 | The Credit Interpretation Request (CIR) to deem diesel generators that are designed to be utilised as a peak energy demand reduction solution is granted conditionally on the project's ability to demonstrate that, although this solution requires significant operational control and investment throughout the building's functional life, it possesses all the attributes necessary for it to be utilised so as to meet the Aim of the Credit. This must be demonstrated by all of the below: - Extract of Specification describing the system to be installed on-site to reduce peak energy demand. - Drawings which illustrate the location and installation of the on-site generation system. - A report prepared by the Electrical Engineer on the peak energy demand reduction system describing the predicted peak-load energy consumption for the building, strategy & system to deliver peak load reduction and the amounts to be provided by the demand reduction system. - A consultant’s advice to the contractor with regards to the design changes. - Evidence that power will be transferred seamlessly (i.e. without any power-outage during transfer);
| x | x | x | x | x | x | x | 2007-08-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | Withdrawn | 3 | - Assessment of the number of days in each month and average duration (measured in hours) that the system will need to be operating, i.e. whenever the load exceeds 75% of the full load. - Evidence that the system is designed to initiate automatically whenever the load exceeds 75% of the full load; - A letter from the Facilities Manager confirming they understand the system will be operated for the aforementioned period, and outlining the full expected expense in running the proposed system (including diesel costs, maintenance etc.); - Evidence of contractual commitment to run the system for at least 5 years following the practical completion of the project; - Evidence that the diesel tank is sized sufficiently to support the operation of the system for one month when it is expected to operate the most; please note that fuel necessary for standby/emergency operation is considered to be in addition to the fuel for peak energy demand reduction; - A clear description of how the diesel tank will be filled, confirming that it can be done conveniently and without disturbance to the building occupants and vehicular and pedestrian traffic; and
| x | x | x | x | x | x | x | 2007-08-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | Withdrawn | 3 | - A letter from the local Council and EPA confirming that they are aware of diesel exhaust associated with such a system and accept that a diesel system will be utilised at frequency and intervals necessary for peak energy demand reduction.
| x | [6 empty] | 2008-01-01 |  | Ene-7 |  |  | Peak Energy Demand Reduction | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to allow energy efficiency initiatives (such as thermal mass, energy efficient envelope, services or lighting) to contribute to the overall reduction of peak energy demand is denied. This credit rewards the installation of specific peak energy demand reduction systems that reduce the pressure on municipal infrastructure; the overall (rather than peak) reduction in the project’s energy demand is already rewarded within the previous credits.
| x | x | x | x | x | x | x | 2008-06-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | CIR Ruling | 5 | The Technical Manual states that “Peak energy demand reduction systems that could comply with the Credit’s requirements include but are not limited to, the following… Photovoltaics (with battery storage)”. The Technical Manual does not technically prevent the use of PV cells being connected to the grid as opposed to a battery storage. Projects are advised to submit the required documentation and ensure that the system installed meets the Credit Criteria as per the Technical Manual. Furthermore, the Certified Assessors will look for evidence that the peak energy demand reduction for any photovoltaic system is deliverable on a worst case scenario, and not in an optimal situation.
|  | x | x | x | x | x | x | 2011-01-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | Correction | 6 | On-site electricity generators Where fuel-based on-site electricity generators (e.g. diesel, biofuel, gas) are used to reduce the building’s peak electricity demand, it must be shown that the fuel tank is sized to support the operation of the system for at least 24 hours at peak load. A fuel tank is not required when the electricity generators are connected to a gas main,
|  | x | x | x | x |  |  | 2011-01-01 |  | Ene-7 | Ene-5 | Ene-3 | Peak Energy Demand Reduction | Technical Clarification | 7 | Addressing 'miscellaneous loads' The technical manual paragraph found under the heading 'Peak Energy Demand Calculations' states: 'Peak energy demand is the predicted annual peak to be calculated as the sum of all distribution bars (to include all miscellaneous loads)...' In this context, 'Miscellaneous loads' does not include equipment installed as part of the fitout.
[8 empty] | 2008-10-01 |  |  |  | Ene-3 | Peak Energy Demand Reduction | Technical Clarification | M1 | The following guidelines apply to projects seeking to achieve this credit: - The same occupancy and usage profiles must be used when calculating the peak energy demand as when calculating the reduced peak energy demand. - Air-conditioning loads from the apartments should only be included if delivered as part of the base building. - The occupant electricity loads shall not be included.
[8 empty] | 2008-10-01 |  |  |  | Ene-3 | Peak Energy Demand Reduction | Technical Clarification | M2 | A naturally ventilated or mechanically assisted naturally ventilated building can be awarded one point under Ene-3 ‘Peak Energy Demand Reduction’ if one point has been awarded for IEQ-4 ‘Thermal Comfort’.
|  |  | x |  | x | x | [5 empty] | Ene-6 | Car Park Ventilation
|  |  |  | x |  |  | x |  |  |  |  | Ene-7 | Unoccupied Areas
[8 empty] | 2008-10-01 |  |  |  | Ene-4 | Unoccupied Spaces | Correction | M1 | In addition to the required documentation stated in the Submission Guidelines, the following documentation is required for this credit: For dwellings: - Tender Electrical Schematic drawings clearly showing the location of the shutdown switch and all relevant connections For common areas: - Extract(s) from the specification where the requirement for an automated lighting control system(s), including any occupant detection and daylight adjustment system(s), has been included. - Tender Electrical Schematic drawings clearly showing the location of motion and daylight sensors
[8 empty] | 2009-02-01 |  |  |  | Ene-4 | Unoccupied Spaces | Correction | M2 | To demonstrate that no air-conditioning has been provided, a letter from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | Ene-7 | Unoccupied Areas | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is naturally ventilated and meets the requirements of IEQ-1 'Ventilation Rates', this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | Ene-7 | Unoccupied Areas | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Tender schematic electrical drawings Projects must submit the following documentation instead: * Tender schematic mechanical drawings All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x | 2009-03-01 |  |  |  | Ene-7 | Unoccupied Areas | Withdrawn | A | Withdrawn on 01/11/2013. Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Tender schematic electrical drawings Projects must submit the following documentation instead: * Tender schematic mechanical drawings All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x |  |  | x | 2009-03-01 |  |  |  | Ene-7 | Unoccupied Areas | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * As Built schematic electrical drawings Projects must submit the following documentation instead: * As Built schematic mechanical drawings All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x | [7 empty] | Ene-8 | Stairs
|  |  |  | x |  |  |  | 2009-03-01 |  |  |  | Ene-8 | Stairs | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x | x | [6 empty] | Ene-9 | Efficient External Lighting
|  |  |  | x |  |  |  | 2009-05-01 |  |  |  | Ene-9 | Efficient External Lighting | Correction | 1 | This Correction applies to all projects registered after this date. Projects registered prior to this date can follow the Technical Manual of this clarification. The Credit Criteria has been changed from: One point is awarded where all externally-lit spaces over the entire site meet the following criteria: - All external lighting has a light source efficacy of at least 50 lumens/watt; - 95% of all external lights are connected to daylight sensors (daylight sensors can be combined with a time switch). Emergency lighting required for BCA compliance is excluded from this credit. To the following: One point is awarded where all externally-lit spaces over the entire site meet the following criteria: - All external lighting has a light source efficacy of at least 65 lumens/watt; - 95% of outdoor spaces meet or exceed the minimum requirements of AS1158 for illuminance levels; and - All external lights are connected to daylight sensors (daylight sensors can be combined with a time switch). Emergency lighting required for BCA compliance is excluded from this credit.
|  |  |  | x | x |  |  | 2009-03-01 |  |  |  | Ene-9 | Efficient External Lighting | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x |  | x | [5 empty] | Ene-10 | Shared Energy Systems / Precinct Energy Systems
[6 empty] | x |  | 2009-10-01 |  |  |  | Ene-10 | Shared Energy Systems / Precinct Energy Systems | CIR Ruling | I1 | The Credit Interpretation Request to deem an on-site renewable energy generation system designed to service a specific system-wide system (such as the operation of the non-potable water distribution system) equivalent to a shared energy system is granted.
[7 empty] | x |  |  |  |  | Ene-11 | Energy Efficient Appliances
[8 empty] | 2009-03-01 |  |  |  | Ene-11 | Energy Efficient Appliances | CIR Ruling | M1 | The following clarification was modified in January 2009 Clothes dryers ammended (from 3.5 stars) ---------------------------- For the purposes of the Green Star – Multi Unit Residential PILOT rating, the ‘best available’ rating for equipment is as follows: - Refrigerators: Single door fridges = 6 stars Two door fridge/freezer = 5 stars Side by side fridge/freezer = 5 stars Freezer chest = 5 stars Freezer upright = 5 stars - Dishwashers = 4 stars - Clothes washers = 5 stars - Clothes dryers = 3 stars - Combined clothes washer and dryer = 7.5* * Please note that this number is the combined total of the ‘washer’ and ‘dryer component’. E.g. the energy star rating for the ‘dryer’ component is 3.5, and the energy star rating for the ‘washer’ component is 4, the combined total is 7.5.
[7 empty] | x | 2011-01-01 |  |  |  | Ene-11 | Energy Efficient Appliances | Technical Clarification | 1 | For an appliance to be 'within one point of the highest available rating': Under the 'Energy Rating' labelling system, the appliance must be a maximum of one star lower than the highest available star rating for a similar appliance. The highest available star rating in this case is considered to be the highest star rating that was available at the time of the project's registration for Green Star certification. e.g. The best available rating was 5 stars at time of registration, so the appliance must be at least 4 star rated; The best available rating was 4.5 stars at time of registration, so the appliance must be at least 3.5 star rated.
[7 empty] | x | 2011-01-01 |  |  |  | Ene-11 | Energy Efficient Appliances | Technical Clarification | 2 | Appliances to be compared using the Australian Government's 'Energy Rating' labelling system must fall within one of the categories listed in the Compliance Criteria for the credit, namely; - Dishwashers; - Clothes washers; - Clothes dryers; and, - Combined clothes washers and dryers. - Refrigerators: - Single-door fridge - Two-door fridge/freezer - Side-by-side fridge/freezer There shall be no further classification within these categories, e.g. a front-loading clothes washer falls in the same category as a top-loading clothes washer. Each appliance must then be compared to others in the finest sizing criteria available on the website. Where a product is on the border of two ranges, the product should form the lower limit of the higher range. For example, a 300L refrigerator should be compared to products in the 300 - 400L range, and a 6kg clothes dryer should be compared to products in the 6 -7kg range. This avoids the issue of under-specifying a product, and should not result in significant over-specification.

## Tra (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Transport
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Tra-0 | Tra-0 | Tra-0 | Tra-0 | General
x | x | x | x | x | x | x | x |  | Tra-2 | Tra-1 | Tra-1 | Tra-1 | Provision of Car Parking
x | x | [6 empty] | 2007-12-01 | Tra-2 | Tra-1 |  |  | Provision of Car Parking / Car Parking | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem this credit 'Not Applicable' (na) due to the remote location and/or absence of local planning allowances is denied. As the environmental impact of automotive commute does not depend on those factors, such an interpretation would counteract the Aim of the Credit.
x | x |  |  |  | x |  |  | 2007-01-01 | Tra-2 | Tra-1 |  |  | Provision of Car Parking / Car Parking | Technical Clarification | 2 | Whenever neither maximum nor minimum local planning allowances exist (e.g., SA, QLD or municipal projects), the project cannot automatically claim the credit but must submit a Credit Interpretation Request (CIR) to substantiate an argument for equivalent yet alternative compliance. Such arguments have been accepted when based on proposed local planning allowances or a sample of other comparable developments in the area. Please see Technical Clarification Tra-2/5 (For Office Interiors) or Tra-1/5 (all other tools) for more information.
x | x | x | x | x | x | x | x | 2008-03-01 | Tra-2 | Tra-1 | Tra-1 | Tra-1 | Provision of Car Parking / Car Parking | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to exclude time-limited service vehicle spaces, as required by Council DCP, is granted conditionally on the project’s ability to demonstrate that time-limited service vehicle spaces are clearly marked and designated for the sole use of these vehicles AND are not available for the use of tenants (i.e. that occupants/users are either physically or punitively precluded from parking in those spaces).
| x | x | x | x | x | x | x | 2008-03-01 |  | Tra-1 | Tra-1 | Tra-1 | Provision of Car Parking | CIR Ruling | 4 | Where no minimum or maximum parking requirements exist and the project chooses to supply no car parks, the project will be eligible for two points.
| x |  |  |  | x |  |  | 2008-01-01 |  | Tra-1 |  |  | Provision of Car Parking | Withdrawn | 5 | The following clarification has been withdrawn. Please see TC No. 10 and 11 for more information (originally posted Jan-08) Mandatory car parking requirements must be used where they apply to the project in the form of local planning allowances or development approval requirements. Where car parking requirements are optional or do not apply to the project, Credit Criteria can be met in any of the following ways: 1) Show that parking is not provided in excess of one parking space per 100m2 of NLA to be awarded one point; 2) Show that parking is not provided in excess of one parking space per 200m2 to be awarded two points; 3) Submit a Credit Interpretation Request (CIR) and gain approval for an equivalent yet alternative method of satisfying the Credit Criteria.
x | [7 empty] | 2007-12-01 | Tra-2 |  |  |  | Provision of Car Parking / Car Parking | CIR Ruling | 6 | The Credit Interpretation Request (CIR) to demonstrate compliance via an alternative benchmark due to the absence of car parking limits provided in the projects DA is denied whenever local planning allowances exist.
x | [7 empty] | 2008-08-01 | Tra-2 |  |  |  | Provision of Car Parking / Car Parking | Technical Clarification | 7 | The Credit Interpretation Request to have a number of allocated parking spaces not counted for purposes of this credit by turning them into dedicated storage area is granted. Please note: This CIR does not automatically grant the points for this credit. The project must still demonstrate via their submission documentation that: - The number of parking spaces remaining comply with the Credit Criteria and Compliance Requirements for the number of claimed points; - The parking spaces have been turned into a dedicated storage area in such a way that they cannot easily be turned back into parking spaces (such as by being enclosed via a stud wall, or via fully enclosing the space via a permanent structure); and - All other criteria required by the technical manual have been met.
x | x | x | x | x | x | x | x | 2008-09-01 | Tra-2 | Tra-1 | Tra-1 | Tra-1 | Provision of Car Parking / Car Parking | Technical Clarification | 8 | Where a project is providing less than the minimum number of car parking spaces allowable by Council, the project must provide evidence of Council approval of their scheme.
|  |  |  | x |  |  |  | 2011-01-01 |  |  |  | Tra-1 | Provision of Car Parking | Technical Clarification | 9 | The credit criteria are assessed by making comparisons between the parking provided, and the parking space allowance imposed by the development approval or the local planning authority. If the parking space allowance applies to an entire site containing several buildings, assessment of the credit criteria must be based on comparisons to the parking space allowance for the site. e.g: An existing school has 270 car parking spaces. The local planning allowance for a new building on a site with existing school buildings, requires a minimum of 300 car parking spaces for the entire school: -One point can be claimed if the total number of car parking spaces for the entire school is 330 spaces or less. -Two points can be claimed if the total number of car parking spaces for the entire school of 300 spaces or less.
x | x | x | x | x | x |  | x | 2011-01-01 | Tra-1 | Tra-1 | Tra-1 | Tra-1 | Provision of Car Parking | Technical Clarification | 10 | Establishing car parking requirements where no local planning allowance exists Where local planning car parking requirements exist, they must be used to determine the number of parking spaces that would meet the Credit Criteria. Where there are no local planning car parking requirements, alternative Credit Criteria can be proposed. A Credit Interpretation Request must be submitted and approved before a proposal can be used to demonstrate compliance with the Credit Criteria. To be approved the proposal must show that it will deliver the environmental outcomes that were intended by the original Credit Criteria. A few examples of research that could be used as a basis for a proposal are: • Conducting a study of the car parking requirements in similar buildings; or • Using local planning allowances of neighbouring jurisdictions; or • Conducting a Traffic Impact Assessment.
x | x | x | [5 empty] | 2011-01-01 |  | Tra-1 | Tra-1 |  | Provision of Car Parking | Technical Clarification | 11 | Projects registered for assessment by Green Star Office Office Interiors, Office v2 and Office v3, may use an alternative method to meet the Credit Criteria: Show that car parking is provided for a maximum of one parking space per 100m2 of NLA to be awarded one point; Show that car parking is provided for a maximum of one parking space per 200m2 to be awarded two points.
| x | x | x | x | x | x | x |  |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces
| x | [6 empty] | 2006-01-01 | Tra-2 | Tra-2 |  |  | Fuel-Efficient Transport / Small Parking Spaces | Withdrawn | 1 | The following clarification has been withdrawn. Please see TC No. 9 for more information (originally posted Jan-06). In order to claim points for this credit, 'small vehicle parking' spaces must be small in accordance with the description in the Green Star technical manual. Signage indicating 'small vehicle parking' cannot be used to convert a parking space into 'small vehicle parking' for the purpose of this credit.
| x | [6 empty] | 2006-01-01 |  | Tra-2 |  |  | Fuel-Efficient Transport / Small Parking Spaces | Technical Clarification | 2 | Small car spaces need to be provided in a fair and equitable manner (e.g. not blocked by other spaces).
| x | [6 empty] | 2007-12-01 |  | Tra-2 |  |  | Fuel-Efficient Transport / Small Parking Spaces | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem this credit 'Not Applicable' (na) due to the remote location and/or absence of local planning allowances is denied. As the environmental impact of automotive commute does not depend on those factors, such an interpretation would counteract the Aim of the Credit.
| x | x | x | x | x | x | x | 2007-12-01 |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to demonstrate compliance via an alternative benchmark due to the absence of car parking limits provided in the projects DA is denied whenever local planning allowances exist.
[8 empty] | 2008-10-01 |  |  |  | Tra-2 | Fuel Efficient Transport | Technical Clarification | M1 | A project can claim N/A for this credit where the only parking provided is dedicated for use by persons with disabilities, as per Additional Guidance for Tra-1 in the Green Star – Office v3 Technical Manual.
|  | x | x | x |  |  |  | 2009-02-01 |  |  | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Technical Clarification | 5 | Correction: The Technical Manual, under Additional Guidance for ‘Small Vehicle Parking’, states that: “The size of a car space specified for a ‘small vehicle’ must be physically reduced and suitably labelled according to the AS/NZS2890.1:2004 minimum (i.e. 4.3m by 5m for most cases. Refer to Australian Standard for more information).” This should read: “The size of a car space specified for a ‘small vehicle’ must be physically reduced and suitably labelled according to the AS/NZS2890.1:2004 minimum (i.e. 2.3m by 5m for most cases. Refer to Australian Standard for more information).”
|  | x | [5 empty] | 2009-04-01 |  |  | Tra-2 |  | Fuel-Efficient Transport / Small Parking Spaces | Correction | 6 | Preferred Parking Spaces Where the Credit Criteria reads: A minimum of 80% of all preferred parking spaces are dedicated solely for use by car‑pool participants, small cars, hybrid or other alternative fuel vehicles. It should say: A minimum of 80% of all spaces designated for use by car‑pool participants, small cars, hybrid or other alternative fuel vehicles must be preferred parking spaces (see definition of 'Preferred Parking Spaces').
|  |  | x | x |  |  |  | 2009-04-01 |  |  |  | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Correction | 7 | The Credit Criteria for this credit have been revised. The Criteria now read as follows: One Point is awarded where: • A minimum of 25% of the total parking spaces on the site are designed and labelled for small cars in accordance with AS/NZS 2890.1:2004 (i.e. maximum 2.3m wide x 5.0m long) and/or mopeds/motorbikes and/or car sharing programs, hybrid or other alternative fuel vehicles; • A minimum of 10% of the total parking spaces or 10 parking spaces (whichever is the greater) must be for small cars; and • A minimum of 80% of all spaces designated for use by car-pool participants, small cars, hybrid or other alternative fuel vehicles are preferred parking spaces (i.e. located near the entrance). If no parking spaces are to be provided, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Transport Category Score.
| x | x | x | x | x | x | x | 2011-01-01 |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Correction | 9 | In order to claim points for this credit, the dimensions of 'small vehicle parking' spaces must be physically limited in width and depth in accordance with the description in the Green Star technical manual. Signage and/or line marking indicating 'small vehicle parking' cannot be used to convert a standard parking space into 'small vehicle parking' for the purpose of this credit.
| x | [6 empty] | 2011-01-01 |  | Tra-2 |  |  | Fuel-Efficient Transport / Small Parking Spaces | Technical Clarification | 10 | Car parking spaces set aside for users with disabilities can be excluded from the total number of car parking spaces in calculations for this credit.
|  | x | x | x | x | x | x | 2009-03-01 |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from the contract. * Confirmation from the building owner. Projects must submit the following documentation instead: * Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Indicating the number of car pool, motorbike, small car, and total number of parking spaces being provided, and referencing the site plans when necessary; - Where alternative compliance is claimed, providing calculations that relate the number of parking spaces provided to the project nominated area; and - Stating that the spaces are designed in accordance with the dimensional requirements for small spaces set out in AS/NZS 2890.1:2004 All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the building owner. Projects must submit the following documentation instead: * Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Indicating the number of car pool, motorbike, small car, and total number of parking spaces being provided, and referencing the site plans when necessary; - Where alternative compliance is claimed, providing calculations that relate the number of parking spaces provided to the project nominated area; and - Stating that the spaces are designed in accordance with the dimensional requirements for small spaces set out in AS/NZS 2890.1:2004 All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Tra-2 | Tra-2 | Tra-2 | Fuel-Efficient Transport / Small Parking Spaces | Documentation | C | Car Sharing program registration is also acceptable evidence to meet the requirements for car-pool participants.
x | x | x | x | x | x | x | x |  | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities
| x | [6 empty] | 2006-06-01 |  | Tra-3 |  |  | Cyclist Facilities | Correction | 1 | The Credit Criteria for the visitor bicycle storage within the Technical Manual had a typographic error. The Criteria should have read: "one space per 750m2 NLA or part thereof" and not "one space per 7500m2 NLA or part thereof". The Technical Manual and the rating tool have been updated. This change does not apply to projects registered prior to 12 Jun-06. All projects registered after 12 Jun-06 will be subject to this correction.
x | x | [6 empty] | 2006-09-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 2 | For owner-occupier projects, cyclist facilities should not be claimed in the base building assessment if the project wishes to claim the Additional Point ("facilities were installed specifically for the tenancy fitout and were not pre-existing in the base building") in the fitout assessment.
| x | x | x | x | x | x | x | 2006-09-01 |  | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 3 | The guidance for sizing lockers is taken from the cited Standards; no specific measurements are implied.
| x | x | x | x | x | x | x | 2007-08-01 |  | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to deem a secondary public entrance (the main public entrance for the deliveries area) equivalent to the major public entrance for the purpose of locating visitor bike storage is denied. Visitor bike storage is not intended for the sole use by couriers; such an assumption is not supported by the Technical Manual or the Aim of Credit. The project can choose to provide visitor parking in excess of the Green Star requirement and provide directional instructions to couriers; however, to be eligible for the additional point, the visitor bike storage must be sufficient, accessible, signposted and located near a major public entrance.
x | x | [6 empty] | 2007-12-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Withdrawn | 5 | The following clarification has been withdrawn, as it contained two clarifications. It has been split and relocated further down within this credit. The Technical Manual states that bicycle storage must be “designed to allow both a wheel and the frame to be locked securely to the structure in accordance with AS 2890.3-1993”. The referenced AS 2890.3-1993 standard actually stipulates that the bike must be able to be locked to both wheels and the frame (see extract below). The standard must be followed. “Even if they are fitted out as showers or changing rooms, the minimum number of toilets for people with disabilities mandated by statutory requirements cannot contribute to the total number of changing or shower facilities provided, as doing so may detract from their availability for use by disabled persons ” (AS 2890.3-1993, bottom of table 1.1).
x | x | [6 empty] | 2008-01-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 6 | The minimum number of toilets for people with disabilities mandated by the BCA cannot contribute to the total number of changing or shower facilities provided, as doing so may detract from their availability for use by disabled persons.
x | x | [6 empty] | 2008-01-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 7 | Even if the toilets for people with disabilities are fitted out as changing rooms, the minimum number of disabled toilets mandated by statutory requirements cannot contribute to the total number of changing facilities provided, as this may detract from their availability for use by disabled persons. Disabled showers can contribute towards the total number of showers provided, as long as they are not stipulated in statutory requirements for the project.
x | x | x | x | x | x | x |  | 2008-01-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 8 | Changing/shower facilities do not have to be aggregated. However, access must be guaranteed and convenient for all building occupants (e.g. not through another tenancy). If changing/shower facilities are located within tenancies rather than in common area, they must be adequately sized for each tenancy based on the default occupancy rate of one person per 15m2, and each location must individually meet the Credit Criteria (e.g. providing excess facilities within one tenancy will not compensate for insufficient facilities in another).
x | x | [6 empty] | 2008-01-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 9 | To support the Aim of the Credit, lockers must be located within the changing facilities. Showers must be located within or immediately adjacent to the changing facilities.
x | x | [6 empty] | 2008-01-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 10 | Changing facilities (with lockers and showers) do not have to be in the same location as the secure bicycle storage. It is not necessary to provide weather-protected access from the secure bicycle storage to the changing/shower facilities. However, the access between the changing/shower facilities and the occupied space (e.g. office) must be weather protected.
| x | x | x | x | x | x | x | 2008-01-01 |  | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Withdrawn | 11 | See clarification Tra-3/19 for more information The Credit Interpretation Request (CIR) to deem a particular bicycle parking system appropriate for meeting the Credit Criteria is granted conditionally on the project’s ability to demonstrate, through its submission for this Credit, how the attributes of this system meet the criteria of AS2890.3.
x | x | x | x | x | x | x | x | 2008-01-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 12 | The Credit Interpretation Request (CIR) to deem the location of visitor bicycle parking in the third level of basement equivalent to “near a public entrance” is denied because the proposed location is not considered to be suitable for visitor bicycle parking and does not meet the Aim of Credit.
x | x | x | x | x | x | x | x | 2008-01-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 13 | The Credit Interpretation Request (CIR) to provide visitor bicycle parking in two different locations is granted conditionally on the projects ability to demonstrate that the two different locations individually meet the Credit Criteria.
| x | x | x | x | x | x |  | 2008-06-01 |  | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 14 | Please note that pedestrian access between office towers via the basement car park is sufficient to meet the requirement for ‘all-weather covered access’. CIR Ruling: The Credit Interpretation Request (CIR) to have one centralised cyclist facility to accommodate the users of both office towers in a development is granted conditionally on the project’s ability to demonstrate that the facility is in close proximity to at least one major public entrance of each office tower that it will service. Compliance with the all other credit requirements in the Technical Manual must also be demonstrated. This ruling applies only to buildings that are on the same title and registered together for one Green Star Certification (i.e. it will not apply to buildings registered for separate Green Star certified ratings; in those cases, however, the ruling on ‘external amenities’ will apply).
x | x | x | x | x | x | x | x | 2008-07-01 |  | Tra-3 |  |  | Cyclist Facilities | Technical Clarification | 15 | The Green Building Council of Australia understands that a number of projects undertaking a refurbishment of an existing building can have difficulties meeting the Credit Criteria for this credit. These may be due to limitations placed by the existing building envelope, authority requirements, building structure or availability of hydraulic services. These projects are advised to submit a CIR if they are unsure as to whether their approach is equivalent to that which is being requested by the Credit Criteria and Compliance Requirements for this credit.
| x | x | x | x | x | x | x | 2008-08-01 |  | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 16 | In order for visitor bicycle facilities to be considered near a major public entrance, these must be located in direct line of sight from a major public entrance of the building and no more than 50 meters away. Where the visitor bicycle facilities are not located within a direct line of sight from a major public entrance, then: - A sign indicating where the visitor bicycle parking spaces are located must be posted at the major public entrance of the building; and - The visitor parking spaces must not be located more than 50 meters away from a major public entrance. Major public entrance is defined as a public entrance to the building that is accessible from a public plaza, main street or avenue (e.g. not the entrance from a side street). Due to the large number of variations within this Credit and the large number of constraints that may exist, projects that cannot achieve these criteria may choose to submit a CIR delineating their specific situation.
x | [7 empty] | 2007-01-01 | Tra-3 |  |  |  | Cyclist Facilities | Technical Clarification | 17 | In Green Star - Office Interiors, this credit addresses tenancy occupants at the prescribed occupancy of 1 occupant per 15 m2 of NLA, not staff and visitors separately like Green Star - Office Design or Green Star - Office As Built.
x | x | [6 empty] | 2009-07-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | Withdrawn | 18 | Originally posted in August 2007. This clarification is covered by Tra-3/6 and Tra-3/7. It has been withdrawn for purposes of clarity. The number of sanitary facilities for people with disabilities mandated by statutory requirements must be excluded from the calculation. The minimum number of sanitary facilities for people with disabilities mandated by the BCA cannot contribute to the total number of changing or shower facilities provided, as doing so may detract from their availability for use by people with disabilities.
x | x | x | x | x | x | x | x | 2008-01-01 | Tra-3 | Tra-3 |  |  | Cyclist Facilities | CIR Ruling | 19 | The Credit Interpretation Request (CIR) to deem any specific bicycle parking system appropriate for meeting the Credit Criteria in respect to bicycle storage is granted conditionally on the project’s ability to demonstrate, through its submission for this credit, how the attributes of this system meet the criteria of AS2890.3.
|  | x | x | x | x | x | x | 2008-09-01 |  |  | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 20 | The following definition (italicised) is being expanded (non-italicised)(Tra-3/16): Major public entrance is defined as a public entrance to the building that is accessible from a public plaza, main street or avenue (e.g. not the entrance from a side street unless the side street is the only entrance to the building). Furthermore, the entrance to a multi-storey carpark will also be considered to be a major public entrance if the visitor’s cyclist facilities are clearly signposted at the entry to the carpark and the designated parking is no more than one split level away (in either direction).
x | [7 empty] | 2008-12-01 | Tra-3 |  |  |  | Cyclist Facilities | Technical Clarification | 21 | Where the base building provides part of the required facilities (e.g enough bicycle racks but not enough showers, or vice versa) tenants can claim the additional point for this credit if the additional facilities are installed for the tenant, and paid for by them. In order to claim the additional point, the project must demonstrate that: - The base building was lacking part or all of the facilities installed by the tenant. The project must submit relevant current As-Built drawings of the base building showing that this is the case; - All showers, lockers, change facilities, or bike racks (both new and existing) meet the requirements stated in the Credit Criteria; and - The required number of facilities as per the technical manual are solely for the use of the tenant undertaking a Green Star Rating.
x | x | x | x | x | x | x |  | 2008-12-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 22 | In a situation where the project provides additional bicycle storage above that required by the Technical Manual, the GBCA recommends that, based on the concept of good design, additional shower and changing facilities also be provided. This will eliminate congestion of the provided amenities and ensure user satisfaction.
x | x | x | x | x | x | x |  | 2008-12-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 23 | Secure lockers must be adequately sized to accommodate normal office clothing, i.e. should not be significantly smaller than 80cm tall by 25cm wide (for box lockers) or 80cm tall by 40cm wide (for ‘L-shaped’ double lockers).
x | [7 empty] | 2008-12-01 | Tra-3 |  |  |  | Cyclist Facilities | Correction | 24 | The Technical Manual states that to claim two points, the project must provide: “secure bicycle storage for 10% of all building occupants (based on one person per 15m2 of the NLA); This should read: “secure bicycle storage for 10% of all tenancy occupants (based on one person per 15m2 of the NLA);
x | x | x | x | x | x | x | x | 2008-12-01 | Tra-3 |  |  |  | Cyclist Facilities | Technical Clarification | 25 | Where base building cyclist facilities are sufficient to provide the required level of service for the claimed percentage of occupants for the whole building, these facilities can be shown as shared (i.e. they do not have to be dedicated to the tenancy), provided that the project can show that the tenant will have access to these facilities. Where such facilities are only sufficient to provide the claimed percentage for a portion of the base building, and not for the whole building, the claimed number of facilities need to be shown as exclusive to the tenancy via a lease agreement or a letter from the building owner.
x | x | x | x | x | x | x |  | 2009-03-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 26 | While unisex facilities can meet the requirements for the credit criteria for this credit, projects must ensure that a level of privacy is provided for the showering and changing of the users (i.e. opaque partitions, private changing facilities adjacent to the showers). The Certified Assessors reserve the right to request justification of how such facilities provide for users' privacy. Please note, while projects are not required to demonstrate compliance with the BCA to be awarded this credit, Project teams are advised to seek professional advice about whether Unisex change facilities are compliant with the BCA.
x | x | x | x | x | x | x |  | 2009-10-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 27 | Additional lockers to the numbers required in the Technical Manual are not subject to the Compliance Requirements for this credit.
x | x | x | x | x | x | x |  | 2009-10-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | CIR Ruling | 28 | The installation of additional storage in the change rooms (in the form of pigeon holes and day lockers) in a number equivalent to that required by the Credit Criteria, and permanent secure lockers in the areas adjacent to the change rooms is an alternative yet equivalent method of meeting the Aim of this Credit. The permanent secure lockers must still be provided in the number and size required by the technical manual.
|  |  |  | x |  |  |  | 2009-10-01 |  |  |  | Tra-3 | Cyclist Facilities | CIR Ruling | 29 | For purposes of this credit, ‘staff room’ is defined as: any area, or office, that is occupied by a, or a number of, staff member(s) in a semi-permanent manner. Examples of staff rooms are administrative offices, reception, staff lounge area, staff offices, and at least three classrooms.
[7 empty] | x | 2011-01-01 |  |  |  | Tra-3 | Cyclist Facilities | Technical Clarification | 30 | Visitor bicycle parking can be located inside or outside the building, visitors must however have access to the area where the parking is located.
|  |  | x |  |  |  |  | 2011-01-01 |  |  |  | Tra-3 | Cyclist Facilities | Correction | 31 | The Credit Criteria for Green Star - Retail Centre v1 states (p.161): 'An additional point is awarded where visitor bicycle storage is provided within 50m of a major public entrance and meets the following criteria:' This is incorrect. Points for visitor cyclist facilities can be awarded, regardless of whether Credit Criteria for staff cycling facilities are met or not. The correct wording is: 'A point is awarded where visitor bicycle storage is provided within 50m of a major public entrance and meets the following criteria:'
| x | [6 empty] | 2011-01-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 32 | Weather protection for cyclist facilities must be justified based on geographic location, or submitted for approval as a CIR. Appropriate measures vary, depending on the predicted weather conditions for the geographic location of a project. For example, appropriate weather protection in Hobart may involve providing shelter from snowfalls, while in Alice Springs shielding bicycles from heat and dust may be more important.
x | x | x | x | x | x | x |  | 2011-01-01 |  |  |  | Tra-3 | Cyclist Facilities | Credit Interpretation Request | 33 | The CIR to deem the location of staff lockers in the immediate vicinity to the change rooms rather than within them, as an alternative yet equivalent form to comply with the intent of the credit is granted.
[7 empty] | x | 2012-08-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Correction | 34 | This is a correction to the Credit Criteria for Tra-3. To achieve the additional point for visitor parking, instead of: “0.25 visitor spaces per dwelling in an accessible on-grade location, signposted and near a major public entrance” The credit criteria for visitor parking is now: “a minimum of 0.1 visitor spaces (rounded up to the nearest whole number) per dwelling in an accessible on-grade location, signposted and near a major public entrance”
|  |  |  | x |  |  |  | 2012-08-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Technical Clarification | 35 | The number of staff and students shall be confirmed by the building owner. To demonstrate staff and student numbers the project team must provide, within their submission, a letter from the building owner: - Stating the number of staff that will work in the building at the same time during a normal day of operation; - Stating the maximum number of students that will be present within the building at the same time during a normal day of operation. For primary and secondary schools, the number of students over grade 4 should be nominated here; - Describing the methodology used to determine the number of staff and students.
|  | x | x | x | x | x |  | 2009-03-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from the specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
x |  | x | x | x | x | x |  | 2009-03-01 | Tra-3 | Tra-3 | Tra-3 | Tra-3 | Cyclist Facilities | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation(s) from the supplier(s). *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x | x | x | x | x | x | x | x |  | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport
x | x | x | x | x | x | x | x | 2007-08-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem the average frequency of services (which individually do not meet the frequency requirements) to be entered into the Public Transport Calculator is denied as services with average frequency intervals greater than 30 minutes are not considered to be of the same benefit to building occupants commuting to work.
x | x | x | x | x | x | x | x | 2007-08-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem the private bus transport system with an established route and timetable equivalent to public transport is granted conditionally on the project’s ability to demonstrate that the future operation of this service is as certain as public transport (i.e. demonstrates alternative but equivalent compliance in respect to longevity, publicity, etc.). Please enter the number and frequency of services into the Public Transport Calculator and provide evidence stipulated in the Compliance Requirements.
x | x | x | x | x | x | x | x | 2008-06-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | CIR Ruling | 3 | The GBCA has introduced a simplified submission methodology for this credit. Projects that meet the requirements outlined in the Deemed to Satisfy Criteria are able to obtain the full five points for this credit. For information on this Deemed to Satisfy Criteria, please click on this cell, or go to the Public Transport DTS tab on this spreadsheet.
x | x | x | x | x | x | x | x | 2008-07-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | Technical Clarification | 4 | The following definition is proposed: For Transportation Hubs, entrance to the transportation hub is defined as the clear entrance to the station as detailed by the transport authority. If the station entrance is within another building, the station entrance is defined as the entrance to the building, provided that the other building entrance is no more than 200 meters to the turnstile / barrier gates.
x | x | x | x | x | x | x | x | 2009-02-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | Technical Clarification | 5 | An expanded Deemed to Satisfy compliance requirement has been created. The document outlines the procedure through which Projects may add new postcodes to the Deemed to Satisfy Provisions Table. The document can be found here in the Public Transport DTS Tab in this spreadsheet.
x | [7 empty] | 2009-02-01 | Tra-1 |  |  |  | Commuting Mass Transport / Public Transport | Technical Clarification | 6 | Where an Office Interiors project has achieved points for this Credit within a Design or As Built rating, they are eligible to claim the same points in Interiors. The submission documentation required is only the Cover Sheet for this Credit, which will need to include the following information: - The Green Star number and name of the Design/As Built project; and - The number of points achieved for this Credit in the Design/As Built rating.
x | x | x | [5 empty] | 2009-03-01 | Tra-1 | Tra-4 | Tra-4 |  | Commuting Mass Transport / Public Transport | Technical Clarification | 7 | A Green Star - Office Interiors project occupying a building that has achieved a Green Star - Design, or Green Star - As Built rating that was awarded any points for Tra-4 'Commuting Public Transport' (for Office v2) or Tra-4 'Commuting Mass Transport' (For Office v3) is automatically awarded the same number of points for this credit. Projects claiming this Deemed to Satisfy methodology must submit the following on their cover sheet: - The Design/As Built project name and number and the number of points achieved for this Credit. Should the project wish to claim additional points all documentation must be provided at the time of submission.
|  | x | x | x | x |  | x | 2011-01-01 |  |  | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | Technical Clarification | 8 | Within the Deemed-to-Satisfy Criteria the following is stated: 'a bus interchange with six bays'. A bay is defined as a bus stop for a 25m bus that allows for independent operation of each bus. This means that arrivals and departures of each vehicle are not physically constrained by other buses. If a bus stop bay serves more than one bus route, it still counted as only one bay.
|  | x | x | x | x | x | x | 2009-03-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | DTS-TRA | A | The ‘Deemed to Satisfy’ methodology for this credit has been expanded to include the distance to major train stations in New South Wales, Queensland and Victoria. This change has been included in the Transport Calculator in all the Green Star excel spreadsheets. This expanded methodology awards points based on the distance to these stations. Project teams that only use this new methodology must simply submit: * Site Plan extending to surrounding areas clearly showing: - The location of the site - The location of the chosen train station - Distance between both. This calculator can be used in conjunction with the other methods outlined in the Technical Manual. For more information on how to use the calculator, please see: http://www.gbca.org.au/technical-clarifications-cir-rulings/transport-deemed-to-satisfy-criteria/1699.htm
| x | x | x | x | x | x | x | 2013-11-01 | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Commuting Mass Transport / Public Transport | Documentation (As Built) | 9 | Points for this credit are automatically awarded, following the successful award of points at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet. Where this approach is adopted, no further documentation is required for this credit. If the project wishes to claim more points than were awarded at the Design stage then full documentation in compliance with the Technical Manual must be provided.
|  |  | x |  |  | x | x |  |  |  |  | Tra-5 | Trip Reduction Mixed-Use
[8 empty] | 2008-10-01 |  |  |  | Tra-5 | Trip Reduction | Technical Clarification | M1 | Examples of amenities for the purpose of this credit include but are not limited to: - Convenience Stores - Pharmacies - Post Offices - Restaurants, Food & Beverage - Gyms, Pools and sport facilities - Hospitals, Clinics and Health Centres - Childcare Centres - Newsagencies - Retail Centres - Cinemas & Theatres - Supermarkets & Grocery Stores - Libraries - ATMs - Community Centres - Schools Please note that this is by no means an exhaustive list, but rather can be used as a guide when submitting for this credit. Where projects are unsure if a proposed amenity meets the relevant critaria, advise must be seeked from the GBCA.
[6 empty] | x |  | 2009-10-01 |  |  |  | Tra-5 | Trip Reduction Mixed-Use | CIR Ruling | I1 | The Credit Interpretation Request to increase the compliant distance from 400m to 1000m is denied as the request is for a change in benchmark rather than an alternative yet equivalent way of demonstrating compliance.
|  |  |  | x | x |  |  | 2009-03-01 |  |  |  | Tra-6 | Transport Design and Planning | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Extract(s) of the specification(s). *Confirmation from the building owner. All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x | x |  |  | 2009-03-01 |  |  |  | Tra-6 | Transport Design and Planning | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * As-built drawings All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  |  | x | x | [6 empty] | Tra-6 | Transport Design and Planning
|  |  |  | x |  |  |  | 2009-10-01 |  |  |  | Tra-6 | Transport Design and Planning | Technical Clarification / CIR Ruling / Correction | 1 | The project is not required to construct pedestrian routes outside the site boundary to link the site to public transport nodes and other nearby amenities to achieve this credit. However, if outside links do exist, the project should connect to those.
[6 empty] | x | [5 empty] | Tra-7 | Proximity to Major Cargo Transport Services

## Wat (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Water
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Wat-0 | Wat-0 | Wat-0 | Wat-0 | General
[8 empty] | 2008-09-01 |  |  |  | Wat-0 | General | Technical Clarification | M1 | The Water Calculator has been amended and uploaded on to the website. Please ensure that the project is using the current rating tool.
x | x | x | x | x | x | x | x | 2011-01-01 | Wat-0 | Wat-0 | Wat-0 | Wat-0 | General | Technical Clarification | 1 | Using off-site reclaimed water is an acceptable way to reduce potable water consumption for Green Star . For Green Star Design ratings, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. A Commisioning report is required for the As-built rating. The reclaimed water system must be operational at the time of practical completion of the building.
x | x | x | x | x | x | x | x | 2011-01-01 | Wat-0 | Wat-0 | Wat-0 | Wat-0 | General | Technical Clarification | 2 | Approval from the relevant local authority is not required for rainwater systems. Evidence of approval from the relevant local authority must be provided for greywater and blackwater systems.
| x | x | x | x | x | x | x |  | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency
x | x | x | x | x | x |  | x | 2007-01-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Withdrawn | 1 | The following clarification has been withdrawn. Please see Technical Clarification No. 24 for more information (originally posted on Jan-07) As custodian closet taps are not an occupant amenity, they are not included in the Potable Water Calculator.
x | x | x | x | x | x |  | x | 2007-01-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 2 | Previously unused water from high-value fresh water sources (e.g., lake, river or bore water) cannot contribute to the amount of non-potable water used. In addition to the surface water table dropping, there is a deficit of groundwater every year, and extracting water from any fresh-water sources merely localises what otherwise would take place on the municipal or state level.
x | x | x | x | x | x |  | x | 2007-12-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 3 | The following is acceptable to demonstrate fitting/fixture performance for the Water Calculator for the first six months after the release of a new product, after which the WELS rating will be required: - a letter from the manufacturer stating the flow rate; and - results of on-site commissioning demonstrating the achievement of the claimed rate.
| x | [6 empty] | 2007-12-01 |  | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 4 | The Green Building Council strongly supports the use of shared/centralised energy or treatment facilities and commends the project on employing this strategy. Both Wat-1 'Occupant Amenity Potable Water Efficiency' and Emi-6 'Reduced Flow to Sewer' can be achieved with a shared plant.
| x | [6 empty] | 2006-01-01 |  | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 5 | The calculator for Water credit Wat-1 'Potable Water Efficiency' has been rectified to address unnecessary disadvantage faced by small rainwater tanks.
x | x | [6 empty] | 2006-06-01 | Wat-1 | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Withdrawn | 6 | See Wat-1 Technical Clarification 8 for more information: For calculating the value (in litres) for dual-flush toilets, please use the 1:2 ration for full:half flush (e.g. enter "4" for 6/3 toilet (as per page 3 of the credit) or "3.3" for 5/2.5 toilet).
x | x | [6 empty] | 2006-06-01 | Wat-1 | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 7 | The National Water Conservation Rating and Labeling Scheme ('A' ratings) formerly ceased on 1Jun-06 and has been superseded by the Water Efficiency Labeling Scheme ('Star' ratings). However, it does not impact the Green Star Potable Water Calculator as all inputs must be in litres. Therefore, please convert either rating to litres to use the Calculator. For more information on the WELS scheme, see www.waterrating.gov.au
x | x | x | x | x | x |  |  | 2006-09-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 8 | In order to determine the water consumption (per flush) of dual-flush toilets for the Calculator, it is appropriate to use the current Green Star method of calculating the ratio of flushes (one full flush to every two half-flushes) OR the WELS calculation method (one full flush to every three half-flushes).
| x | [6 empty] | 2006-09-01 |  | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 9 | If your project sub-meters all water going into the building AND all water going out (for cooling towers), and if the remainder equates to the bathroom water consumption, it is not necessary to have a separate bathroom water meter.
x | x | x | x | x | x |  | x | 2006-09-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 10 | Refurbishment projects ONLY: Waterless urinals can be deemed 'waterless' without completely removing existing plumbing, if the water supply to them has been permanently disabled (i.e. physically dismantled in such a way that reconnection of water supply for flushing is NOT an option without additional construction work).
| x | x | x | x | x |  | x | 2008-01-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 11 | It is understood that in many cases, the relevant Authority will not grant approval of the water reuse/recycling systems until they have been commissioned. For a Green Star Design submission it is acceptable to provide the Authority’s preliminary approval, or if no objection to the system(s) by the authority, the documented design of the system(s) on the basis of relevant State and Local standards. The Authority must confirm that it is only able to approve operational systems. The Authority’s subsequent approval of the operation system(s) may be conditional on the project’s ability to clearly demonstrate compliance with relevant regulation or standards, which may be cited. The relevant authority’s approval of the operational system(s) will still be necessary to confirm compliance for a Green Star As Built submission.
| x | x | x | x | x |  | x | 2008-08-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 11 | Where the relevant Authority cannot provide an approval, preliminary approval, or objections to the system at the time of submission, and where the Authority has a set of published guidelines stating the requirements for a blackwater system, then the following must be provided instead: - Confirmation from the authority that neither approval, nor preliminary approval, nor objections to the system can be provided at this stage; - Confirmation from the hydraulics engineer engaged in the project stating that the blackwater system meets the published guidelines; - Extracts from the authority’s published guidelines that state the relevant criteria applicable to this project. The relevant passages must be highlighted; and - The cover letter/Short Report (required in the Technical Manual) from the hydraulics engineer must include a clear comparison showing how the system meets the criteria outlined in the authority’s published guidelines.
| x | x | x | x | x |  | x | 2008-01-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 12 | If showers are installed but no points are claimed under Tra-3 ‘Cyclist Facilities’, projects do not have to document the water efficiency of the showerheads and can choose ‘no showers installed’ from the drop-down menu of the Potable Water Calculator. Please note that this will affect the calculation of the total amount of greywater generated, and may significantly reduce the amount of greywater deemed available to offset potable water demand.
| x | x | x | x | x |  | x | 2007-12-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 13 | Victoria projects ONLY: The Green Building Council of Australia has been made aware that Victoria has no relevant Authority to approve water collection/re-use systems. In that case, please include the following information in the Credit Cover Sheet of your submission: "The Green Building Council of Australia has been made aware that Victoria has no relevant Authority to approve water collection/re-use systems. Until this changes, the GBCA has ruled that a short report from a qualified hydraulics engineer will be 'deemed to comply' in place of an approval from the relevant Authority (as stipulated in the Technical Manual), if the short report states that the water collection and re-use systems comply with the relevant NSW standards".
| x | x | x | x | x |  | x | 2008-03-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | CIR Ruling | 14 | The Credit Interpretation Request (CIR) to allow the discharge water from the cooling towers to be used for toilet flushing is granted conditionally on the project’s ability to demonstrate that measures have been taken to address health risks posed by using this discharged water have been minimised (e.g. through approval from a relevant authority). Due to the limitations of the Potable Water Calculator, please enter the discharged water amount as ‘greywater’. Please note that this merely compensates for the current limitations of the Calculator and does not alter the definition of greywater.
| x | [6 empty] | 2008-07-01 |  | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 15 | The Green Star – Office Design v2 and Green Star – Office As Built v2 Technical Manual contains a typo (the Calculator is not affected by this typo). In Wat-1 ‘Occupant Amenity Potable Water Efficiency’ on p.2 of 8, it reads: If there are no urinals then an average WC usage of 1.3 per person per day is assumed for all occupants. This should read: If there are no urinals then an average WC usage of 2.3 per person per day is assumed for all occupants.
| x | [6 empty] | 2008-08-01 |  | Wat-1 |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 15 | The following clarification is an expansion on the above: Where the authority cannot provide approval, preliminary approval, or objections to the system at the time of submission, and where the authority has a set of published guidelines stating the requirements for a blackwater system, then the following must be provided instead: - Confirmation from the authority that neither approval, nor preliminary approval, nor objections to the system can be provided at this stage; - Confirmation from the hydraulics engineer engaged in the project stating that the blackwater system meets the published guidelines; - Extracts from the authority’s published guidelines that state the relevant criteria applicable to this project. The relevant passages must be highlighted; and - The cover letter/Short Report (required in the Technical Manual) from the hydraulics engineer must include a clear comparison showing how the system meets the criteria outlined in the authority’s published guidelines.
| x | x | x | x | x |  | x | 2008-08-01 |  | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | CIR Ruling | 16 | The Credit Interpretation Request (CIR) to deem the approval of a test plant equivalent to the preliminary approval of the system for a Green Star submission is granted conditionally. Please note the following: The GBCA accepts that preliminary approval of a ‘test system’ (defined as a test of the full system) within a building is sufficient. However, the relevant Authority must confirm that if the test is successful, then there would be no objection to the ongoing use of the final system within the building. The project will need to provide confirmation from the approval Authority stating that it will only approve the operational system after testing, as per the above Technical Clarification. All other documentation required by the Technical Manual must be provided for as per the Wat-1/Emi-6 credits.
x | [7 empty] | 2009-05-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency | Withdrawn | 17 | Originally posted Jun-06. Please see Clarification no. 21 for more information. The Potable Water Calculator assesses AMENITY fixtures and fittings. Most of the time this will be limited to base building fixtures/fittings, but an executive en suite, for example, would also need to be included.
x | [7 empty] | 2006-06-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 18 | Fitouts do not get credit for water recycling initiatives of the base building (the Technical Manual presents a false notion that it should, while the Calculator does not take that into account).
x | [7 empty] | 2006-09-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 19 | The Potable Water Calculator is not intended to reward fitouts for such base building initiatives as rainwater harvesting or grey- or blackwater recycling. However, if those initiatives were tenant-initiated, the fitout may qualify for Innovation credit. Please provide clear evidence (i.e., proof of payment) of the tenant's contribution to the installation of non-potable water systems.
x | [7 empty] | 2007-12-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Withdrawn | 20 | This clarification has been withdrawn. It was originally posted on Dec 2007. See TC No. 22 for more information. Although 5A-rated dishwashers are not available in Australia, project can use the 5A water consumption in litres as performance criteria, and demonstrate equivalent savings of potable water. This credit is included in order to communicate the need for change to the supplier industry. Within this credit, a point can only be awarded for dishwashers where it is demonstrated that the dishwasher(s) installed are equivalent to 5A rated, independent of occupant behaviour. Please use the data provided in the Table below to ascertain the performance of a 5A dishwasher. Alternatively, to make this point in Wat-1 ‘na’, the project can demonstrate that no dishwashers are installed. See: http://www.waterrating.gov.au/publications/pubs/strategic-study.pdf for more information or the Wat-1 Table tab in this spreadsheet. See the Wat-1 Table No.1 for more information
x | [7 empty] | 2009-05-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency | Withdrawn | 21 | Withdrawn 01-Jul-12. This has been clarified within ruling #30. The Potable Water Calculator assesses all fixtures and fittings except Janitor’s fixtures/fittings, which are excluded. The assessment includes any additional items installed by the project, such as additional showers, toilets and wash hand basin taps as well as items already existing in the Base Building. Please note that kitchenette fixtures/fittings are excluded.
x | [7 empty] | 2009-07-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 22 | For the additional point in this credit, WELS 5 star rated dishwashers are equivalent to 5A rated dishwashers for purposes of Green Star.
[6 empty] | x |  | 2009-10-01 |  |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | CIR Ruling | 23 | Points can be claimed in the Green Star potable water calculator for the use of recycled water treated to Class A+ as replacement of potable water.
x | x | x | x | x | x | x | x | 2011-01-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency | Technical Clarification | 24 | Water consumption will not be altered significantly by reducing the water flow of certain fixtures and fittings. These fittings include: • Bath taps; • Laboratory taps; and • Taps dedicated for cleaning, facility management. These fittings are excluded from assessment for this credit.
|  | x | x | x | x | x | x | 2011-01-01 |  |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency | Correction | 25 | Documentation requirements are being modified. All projects seeking a Green Star – As Built rating must provide the following, in addition to what is required in the Technical Manual: For each fitting and fixture entered in the ‘Potable Water Calculator’ with a flow rate, provide WELS certificates or extracts from the online WELS database.
x | x | x | x | x | x | x | x | 2011-01-01 |  |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency | Technical Clarification | 26 | Installing flow restrictors is recognised as a way to increase the water efficiency of taps. In order for flow restrictors to be recognised for this credit, it must be demonstrated that they cannot be easily removed by building occupants. This can be achieved by installing flow restrictors in pipework, or installing flow restrictors that require specialist tools to make any adjustments to the flow.
x | x | x | x | x | x | x | x | 2011-01-01 |  |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency | Technical Clarification | 27 | Installing flow restrictors is NOT recognised as a way to increase the water efficiency of shower fittings. Water efficiency of shower fittings for this credit must be demonstrated by using the 'Water Efficiency Labelling and Standards Scheme' (WELS). WELS rating for showers includes any components supplied with the shower head. Flow restrictors are often included in the supply of shower heads. The performance of shower heads is generally adversely affected by the installation of water flow restrictors that were not included in the supply of the shower fittings. The WELS rating may be invalidated by the installation of further flow restrictors. For more information about WELS, see AS6400 'Water efficient products - Rating and labelling'.
x | x | x | x | x | x | x | x | 2011-01-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency | Technical Clarification | 28 | Equipment required by regulations for OH&S and emergencies, are excluded from assessment for this credit. Some examples of equipment that may be excluded under these conditions are: • Safety wash stations and • Emergency deluge showers
[8 empty] | 2009-10-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | CIR Ruling | P | The Credit Interpretation Request to use bore water from an aquifer with managed recharge as replacement of potable water in non-potable water applications is denied. The environmental benefit of using water from an aquifer for this purpose is not deemed equivalent to using water from the sources currently recognised in Green Star (for example rainwater collection or greywater).
x | [7 empty] | 2011-01-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Technical Clarification | 29 | The ‘Additional Point’ is ‘Not Applicable’ when zero points are awarded in the Credit Criteria.
x | [7 empty] | 2012-08-01 | Wat-1 |  |  |  | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Correction | 30 | The following items should be included in the Potable Water Calculator: - Fittings and fixtures already existing in the base building. - Fittings and fixtures installed by the project such as additional showers, toilets and wash had basins. The following items should be excluded from the Potable Water Calculator: - Fittings and fittings for the use of janitors/cleaners. - Kitchenette fixtures and fittings.
| x | x | x | x | x |  |  | 2013-11-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Correction | 31 | The 'Potable Water Calculator Guide' referred to in the Compliance Requirements is not available. Project teams must comply with all requirements outlined in the Technical Manual.
|  | x | x | x |  |  |  | 2009-03-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Documentation Guideline | A | Where no rainwater collection or water reuse systems are present or no automatic controls are present, the following is NOT required: * Tender hydraulic schematic drawings Furthermore, for all fixtures and fittings, projects can substitute Extract(s) from the specification(s) with Fittings and Fixtures Schedule provided that the schedule clearly show all hydraulic fixtures and fittings in the project. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Withdrawn | B | This ruling has been withdrawn as of 1-Nov-13. Please refer to Documentation (As Built) C. Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation(s) from the supplier(s). * Confirmation from the contractor. Where no rainwater collection or water reuse systems are present or no automatic controls are present, the following is NOT required: * As built hydraulic schematic drawings Projects must submit the following documentation instead: * Fixtures and Fittings Schedule listing and describing all hydraulic fixtures and fittings in the project and their flow rates. All other documentation must be provided as per the Technical Manual at the time of submission.
|  |  | x | x |  |  |  | 2013-11-01 | Wat-1 | Wat-1 | Wat-1 | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Documentation (As Built) | C | In a Green Star – As Built submission for this credit, in place of the following documentation: • Confirmation(s) from the supplier(s); and • Confirmation from the contractor. It is acceptable to submit the following: • As Built Fixtures and Fitting Schedule - listing and describing all hydraulic fixtures and fittings in the project and their flow rates. In a Green Star – As Built submission for this credit, where no rainwater collection or water reuse systems are present or no automatic controls are present, the following documentation is NOT required: • As built hydraulic schematic drawings - showing the location of all water reuse, collection and storage systems. All other documentation requirements not mentioned here remain applicable.
| x | x | x | x | x | x | x |  |  | Wat-2 | Wat-2 | Wat-2 | Water Meters
| x | [6 empty] | 2006-01-01 |  | Wat-2 |  |  | Water Meters | Technical Clarification | 1 | Kitchenette and other additional non-bathroom sinks (regardless of number) can be on the metered bathroom water line (e.g., use water already metered according to the Credit Criteria).
| x | [6 empty] | 2007-09-01 |  | Wat-2 |  |  | Water Meters | Technical Clarification | 2 | If your project sub-meters all water going into the building AND all water going out (for cooling towers), and if the difference equates to bathroom water consumption, it is not necessary to have a separate bathroom water meter.
| x | [6 empty] | 2007-09-01 |  | Wat-2 |  |  | Water Meters | Technical Clarification | 3 | One meter for ALL bathrooms, as long as it covers both hot and cold water, is sufficient regardless of the size of the building.
| x | x | x | x | x |  | x | 2008-08-01 |  | Wat-2 | Wat-2 | Wat-2 | Water Meters | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to deem an As Built BMS point schedule equivalent to a Design BMS point schedule is granted. Please note that the As Built point schedule must still show the relevant information as required in the Technical Manual.
| x | [6 empty] | 2008-09-01 |  | Wat-2 |  |  | Water Meters | Technical Clarification | 5 | CIR Ruling: The Credit Interpretation Request (CIR) to deem a water use monitoring system equivalent to a BMS system for the purposes of this credit is granted conditionally on the projects ability to demonstrate that: - The system has been properly configured to alert the relevant personnel of any leak both during and outside operating hours; - The system is capable of and configured to determine where the leak(s) are happening and inform the relevant personnel of this; and - The system is installed in all major water uses.
| x | x | x | x | x | x | x | 2011-01-01 |  | Wat-2 |  |  | Water Meters | Technical Clarification | 6 | A BMS point schedule is not required as documentation for Wat-2 Water meters in the design submission.
[8 empty] | 2008-08-01 |  |  |  | Wat-3 | Water Meters | CIR Ruling | M1 | The Credit Interpretation Request to have an independent water meter in each unit/apartment, which monitors the major water uses and can be checked by the unit’s occupants, that is not connected to the building’s general BMS system be deemed equivalent to having a building wide BMS system which monitors the major water uses within the apartment is granted conditionally on the project’s ability to demonstrate that: - Water meters that monitor the building’s major water uses, except for those uses within each unit/apartment, are installed; - These base building water meters are connected to the building’s building management system; - Water meters that monitor each unit/apartment’s major water uses are installed in each unit; - These individual water meters are connected to a visual display which displays the unit’s water usage; and - The visual display is located within each unit and can be easily seen and read by the unit’s occupant.
[8 empty] | 2009-10-01 |  | Wat-2 | Wat-2 | Wat-2 | Water Meters | Technical Clarification / Correction | P | A leak detection system that compares trend data to initial water consumption is not acceptable as it is based on the assumption that no leaks occurred during the initial evaluation period
[8 empty] | 2009-10-01 |  |  |  | Wat-2 | Water Meters | CIR Ruling | Pilot | The Credit Interpretation Request (CIR) to deem a precinct wide BMS system equivalent to a building BMS is granted conditionally. It is noted that the precinct wide BMS system provides information that can be accessed by the building operator through an intranet connection. The project must demonstrate in their submission via a short description in the short report, how the BMS system is intended to be accessed by all building managers; and how the system will alert both the relevant building manager and the precinct manager.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-2 | Wat-2 | Wat-2 | Water Meters | Documentation (Design) | A | Where no automated monitoring system is present, the following is NOT required: * Extract(s) from the specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-2 | Wat-2 | Wat-2 | Water Meters | Documentation (As Built) | B | The Extract(s) from the Commissioning Report must show that the water meter are reading correctly. Furthermore, a copy of the output report of the system must be included in the submission.
| x | x | x | x | x | x | x |  |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation
| x | x | x | x |  |  |  | 2007-01-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation / Landscape Irrigation Water Efficiency | Technical Clarification | 1 | Previously unused water from high-value fresh water sources (e.g., lake, river or bore water) cannot contribute to the amount of non-potable water used. In addition to the surface water table dropping, there is a deficit of groundwater every year, and extracting water from any fresh-water sources merely localises what otherwise would take place on the municipal or state level.
| x | x | x | x | x |  | x | 2006-01-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation / Landscape Irrigation Water Efficiency | Technical Clarification | 2 | Victoria projects ONLY: The Green Building Council of Australia has been made aware that Victoria has no relevant authority to approve water collection/re-use systems. In that case, please include the following information in the Credit Cover Sheet of your submission: "The Green Building Council of Australia has been made aware that Victoria has no relevant authority to approve water collection/re-use systems. Until this changes, the GBCA has ruled that a short report from a qualified hydraulics engineer will be 'deemed to comply' in place of an approval from the relevant authority (as stipulated in the Technical Manual), if the short report states that the water collection and re-use systems comply with the relevant NSW standards".
|  | x | [5 empty] | 2008-10-01 |  |  | Wat-3 |  | Landscape Irrigation | Correction | 3 | Applies to all projects registered from November 2008 Under Evidence for Green Star – Office Design assessment section, the Short Report states under the fourth bullet point: “referencing the as-built hydraulics drawings, the commissioning report extracts and compliance with EPA requirements when necessary”. As this is the evidence requirement for a Green Star – Office Design rating, this should read: “referencing the tender schematic hydraulic drawings, the extracts from the specification(s) and nominating how the relevant EPA compliance can/will be achieved ”.
| x | [6 empty] | 2009-07-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation | Technical Clarification | 4 | Projects with a xeriscape garden can claim 'NA' for this credit. To do so, the project must provide the documentation as per the Green Star – Office Design v2 Technical Manual, as well as: - A landscape report justifying why the design can be classified as ‘xeriscaping’, and - Confirmation of xeriscape garden installation from the owner indicating that the provision of irrigation systems for the xeriscape garden (where provided) will be removed within three months of installation of the landscaping.
|  | x | x | x | x |  | x | 2009-10-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation | Technical Clarification | 5 | The reduction in potable water consumption is to be estimated against the amount of potable water that would be used in the most common solution permitted under the water restrictions in force on the date the project was registered.
|  | x | x | x | x |  | x | 2011-01-01 |  |  |  | Wat-3 | Landscape Irrigation | Technical Clarification | 6 | Additional Guidance' about ‘Reduction in Potable Water Demand’, described for this credit in the technical manual: ‘…The Potable Water Calculator does not undertake detailed calculations of water storage efficiency. However, the storage tank must have a minimum of 20 days’ storage capacity for the toilet flushing demand entered’ This minimum requirement for storage capacity only applies to rainwater harvesting. It does not apply to use of greywater or blackwater.
|  | x | x | x | x | x | x | 2009-03-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where irrigation systems are installed: * Short Report * Tender schematic hydraulic drawings Projects must submit the following documentation instead Where irrigation systems are installed: * Short report by a suitably qualified professional detailing: - The proposed landscape irrigation system, its water sources and operation; - Providing calculations (and justifying values used) for the reference case; - Demonstrating how the proposed system meets the Credit Criteria against the reference case; and - Referencing the drawings, the extract(s) from the specification and compliance with relevant authority approval when necessary. * Tender drawings - Indicating the design, location and water supply of the irrigation system of the system; and - Specifically showing that the tank size is the same as that calculated. All other documentation must be provided as per the technical manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: Where xeriscape garden is installed * Landscape report * Confirmation of xeriscape garden installation Projects must submit the following documentation instead Where xeriscape garden is installed * Short report by a suitably qualified professional justifying why the design can be classified as ‘xeriscaping’; * Site Plan of the entire site showing the use of each area (including roofs) and clearly indicating the location (or lack of) any landscaped area. Furthermore, the Extract(s) from the Commissioning Report must show that the control strategies of the landscape irrigation work as intended, in addition to the requirements stated in the Technical Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2013-11-01 |  | Wat-3 | Wat-3 | Wat-3 | Landscape Irrigation | Documentation | C | Where the project team is claiming that 100% of irrigation water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. As such, the documentation requirements have been amended as follows: Short Report by a suitably qualified engineer detailing: • The proposed landscape irrigation system and its water sources and operation; • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection). • Reference to how each of the demands is connected to the non-potable water supply; • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water; and • Referencing the hydraulics drawings (Tender or As Built dependent on the certification sought) and the extracts from specifications (Design submission) or commissioning report (As Built submission). All other documentation requirements not mentioned here remain applicable.
| x | x | x | x | x | x | x |  |  | Wat-4 | Wat-4 | Wat-4 | Heat Rejection Water / Cooling Tower Water Consumption
[8 empty] | 2007-01-01 |  | Wat-4 |  |  | Cooling Tower Water Consumption | Technical Clarification | 1 | Previously unused water from high-value fresh water sources (e.g. lake, river or bore water) cannot contribute to the amount of non-potable water used. In addition to the surface water table dropping, there is a deficit of groundwater every year, and extracting water from any fresh-water sources merely localises what otherwise would take place on the municipal or state level.
[8 empty] | 2007-08-01 |  | Wat-4 |  |  | Cooling Tower Water Consumption | Technical Clarification | 2 | For mixed-mode ventilated buildings, it must be clearly demonstrated that the predicted reduction in the operating hours of the mechanical ventilation system does in fact equate to the stipulated reduction in potable water consumption.
[8 empty] | 2007-08-01 |  | Wat-4 |  |  | Cooling Tower Water Consumption | Technical Clarification | 3 | Please note that 50% reduction in operating hours does not equate, under most circumstances, to a 50% reduction in water consumption by cooling towers.
[8 empty] | 2009-02-01 |  |  |  | Wat-4 | Heat Rejection Water | Correction | M1 | A letter, from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
| x | [6 empty] | 2009-03-01 |  | Wat-4 | Wat-5 | Wat-6 | Cooling Tower Water Consumption/Heat Rejection Water | CIR Ruling | 4 | This CIR was previously incorrectly targeted within Green Star - Office v3, Green Star - Education v1, Green Star - Retail Centre v1 and Green Star - Healthcare v1. For those tools, see the relevant technical manual. The CIR to deem the reduction of potable water derived from the design or installation of an alternative water-based heat rejection system equivalent to a cooling tower operating at six cycles of concentration is granted conditionally on the project’s ability to demonstrate that: - The selected system’s water consumption is equivalent to that of a cooling tower operating at six cycles of concentration installed in the same project (i.e. calculations cannot be shown to be done on a standard building, on an unspecified location); - The selected system is modelled to achieve the water reduction equivalent to the cooling tower while providing the same level of performance; and - Alll calculations and values are properly justified in the submission.
|  | x | x | x | x |  |  | 2009-03-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | DTS | DTS-NV | For purposes of this credit, where the building is claiming IEQ-1 'Ventilation Rates' by meeting the requirements for 'Naturally Ventilated Spaces' this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation (Design) | A | For mechanically air-conditioned spaces, projects may provide, in place of the Tender schematic hydraulic drawings, other Tender drawings, such as mechanical drawings, provided that the information requested in the Technical Manual has been included.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation (As Built) | C | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: For naturally ventilated and mechanically assisted naturally ventilated spaces: * Extract(s) from the commissioning report
|  | x | x | x | x |  | x | 2013-11-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation | D | Where the project team is claiming that 100% of heat rejection water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. As such, the documentation requirements have been amended as follows: In the Short Report, in lieu of: • Providing calculations (and justifying the values used) for the reference case; and • Demonstrating how the proposed system meets the credit criteria against the reference case. The following must be included: • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection) the calculation for cooling demand must reflect the thermal model used for Ene-1 Greenhouse Gas Emissions with specific refernce to peak events. • Reference to how each of the demands is connected to the non-potable water supply; and • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water. All other documentation requirements not mentioned here remain applicable.
[6 empty] | x |  | 2013-11-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation | E | Where the project team is claiming that 100% of heat rejection water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. In the Short Report, in lieu of the information required for a reference case (text highlighted red): • Where water-based heat rejection system(s) are present, detailing any heat rejection system(s) in the project; providing calculations and justifying the values used; and describing how the proposed system meets the credit criteria against the reference case with specific reference to peak events. The following must be included: • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection). • Reference to how each of the demands is connected to the non-potable water supply; and • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water. All other documentation requirements not mentioned here remain applicable.
|  | x | x | x |  |  |  | 2013-11-01 |  | Wat-4 | Wat-4 | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation (As Built) | F | For mechanically air-conditioned spaces, projects may provide, in place of the As Built hydraulic drawings, other As Built drawings, such as mechanical drawings, provided that the information requested in the Technical Manual has been included.
| x | x | x | x | x | x | x |  |  | Wat-5 | Wat-5 | Wat-5 | Fire System Water Consumption
[6 empty] | x |  | 2012-08-01 |  | Wat-5 | Wat-5 | Wat-5 | Fire System Water Consumption | Correction | 1 | The Compliance Requirement in Wat-5 'Fire System Water' in Green Star – Industrial v1 for drain-down areas no greater than 1000m2 is withdrawn. Instead, it must be shown there is a minimum of one drain-down area per floor in each building, and that drain-down areas are sized to be no greater than those specified in section 2.3.2 of AS2118.1-2006.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-5 | Wat-5 | Wat-5 | Fire System Water Consumption | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from the specification(s) All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Wat-5 | Wat-5 | Wat-5 | Fire System Water Consumption | Documentation (Design) | B | Where the credit is claimed as 'Not Applicable', projects can submit either the Copy of the Development Approval, or Extract(s) from the fire engineering report. Both are not required to claim the credit.
|  |  |  | x | x | [6 empty] | Wat-6 | Potable Water Use in Laboratories/Equipment
|  |  |  | x |  |  |  | 2013-11-01 |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Correction | 1 | The Documentation Guidelines - Design as detailed in the Technical Manual are withdrawn and replaced by: Documentation Guidelines - Design Submit all the evidence and ensure it readily confirms compliance. o Short report o Extract(s) of the specification(s) o Tender schematic hydraulic drawings If the credit is claimed due to there being no once-through cooling system installed o Short report Where the credit is claimed as ‘Not Applicable’: o Confirmation from the architect o Tender drawings Short report by a suitably qualified hydraulic engineer: • Detailing the proposed laboratory equipment for cooling, it's water sources and operation; • Demonstrating how the proposed system meets the Credit Criteria; and • Referencing specification extract(s) and tender schematic hydraulic drawings when necessary. If there is no once-through cooling: • Demonstrating that no once-through cooling systems are installed. Extract(s) from the specification(s) identifying the proposed water-using equipment, its water sources and operation requirements. Tender schematic hydraulic drawings indicating the design, location and water supply of the equipment cooling system. Confirmation from the architect referencing the tender drawings; • That less the 10% of the buildings nominated area is devoted to laboratories; OR • That no laboratories are included in the building. Tender drawings showing the use of each area within the buildings and clearly indicating the percentage of laboratories within the project.
|  |  |  | x |  |  |  | 2013-11-01 |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Correction | 2 | The Documentation Guidelines - As Built as detailed in the Technical Manual are withdrawn and replaced by: Documentation Guidelines - As Built Submit all the evidence and ensure it readily confirms compliance. o Short report o Extract(s) from the Commissioning Report o As Built hydraulic drawings If the credit is claimed due to there being no once-through cooling system installed o Short report Where the credit is claimed as ‘Not Applicable’: o Confirmation from the architect o As Built drawings Short report by a suitably qualified hydraulic engineer: • Detailing the proposed laboratory equipment for cooling, it's water sources and operation; • Demonstrating how the proposed system meets the Credit Criteria; and • Referencing the As Built hydraulic drawings and the Commissioning Report extracts when necessary. If there is no once-through cooling: • Demonstrating that no once-through cooling systems are installed. Extract(s) from the Commissioning Report demonstrating that the system has been commissioned and operates as intended by the design, and as expressed in the hydraulics report. As Built hydraulic drawings indicating the design, location and water supply of the laboratory equipment cooling system. Confirmation from the architect referencing the As Built drawings; • That less the 10% of the buildings nominated area is devoted to laboratories; OR • That no laboratories are included in the building. As Built drawings showing the use of each area within the buildings and clearly indicating the percentage of laboratories within the project.
|  |  |  | x |  |  |  | 2013-11-01 |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Technical Clarification | 3 | For As Built projects For projects where the design of the building has not changed, and the total area of laboraties present within the building has not changed then this credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet and include a note stating that the building design has not changed. Where this approach is adopted, no further documentation is required for this credit. If the building areas have changed, or the area of laboratory has increased, then full documentation in compliance with the Technical Manual must be provided.
[7 empty] | x |  |  |  |  | Wat-7 | Water Efficient Appliances
[7 empty] | x |  |  |  |  | Wat-8 | Swimming Pool / Spa Water Efficiency
[8 empty] | 2008-10-01 |  |  |  | Wat-7 | Swimming Pool/Spa Water Efficiency | CIR Ruling | M1 | The Credit Interpretation Request (CIR) to utilise rainwater for pool makeup water is granted. The applicant will be required to demonstrate through provision of calculations and specifications that the supply of rainwater is adequate to achieve the 70% reduction target.
[7 empty] | x | 2012-08-01 |  |  |  | Wat-8 | Swimming Pool/Spa Water Efficiency | Correction | 1 | This ruling is a clarification that spas are also subject to the requirements of this credit. This is not a change to the credit requirements, this is simply providing further clarification. Two points are awarded where it is demonstrated that: • A pool blanket and a spa blanket is included to prevent water loss from evaporation; and • The total potable water consumption has been reduced by at least 70% through either or a combination of: –– Efficient swimming pool and spa filtration system compared to traditional sand filtration; –– Backwash water is collected and treated for re-use on-site; and –– The pool and spa make-up water is non-potable water. Where no swimming pool or spa is included in the development, this credit is ‘Not Applicable’ and is excluded from the points available to calculate the Water Category Score.

## Mat (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Material
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General
x |  |  |  | x | x |  | x | 2007-08-01 |  | Mat-0 |  | Mat-0 | General | Technical Clarification | 1 | To claim 'reused' items, a statement from the Interior Designer (DIA or IAID) and supporting evidence must clearly demonstrate that the items were previously used. If the Specification states that the item must be reused, a statement from the Interior Designer must confirm that the specified item was installed on site. The following can also be used as evidence by the Interior Designer: - The final schedule of furniture, fitting and finishes; - Purchase receipts should the items have been acquired from a second-hand retailer; and - A removalists inventory from the previous location of the item.
x | x | x | x | x | x | x | x | 2008-07-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General | Technical Clarification | 2 | Contract Value The Contract Value is defined as the dollar value that will be required to complete the works for the entire project, including site works (landscaping, external paving, etc). There are a number of Credits [e.g. Concrete (Mat-4/Mat-5) , ‘Steel (Mat-5/Mat-6), Sustainable Timber (MAt-7/Mat-8)] that reference this definition. As such, the following must be excluded when using the contract value for calculations of such Credits: - Demolition works; - Consultants, design fees, project management fees; - Works outside the site area; and - Buildings or areas within the site that are not being assessed for purposes of Green Star. Where a number of amenities or services are shared between buildings, the GBCA expects that the cost apportioned to the rated building is equivalent to the use that the building will have of these facilities (e.g. if a shared parking has 100 spaces but 40 are being allocated to the Green Star-rated building, then 40% of the carpark cost must be allocated to the project’s contract value). Please submit a letter from a Quantity Surveyor or cost planner showing a break down of the excluded costs and the total cost for the project undergoing the Green Star rating.
x |  |  |  | x | x |  | x | 2008-03-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 3 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA license agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding Round 1 submission, from the GECA website products register are sufficient evidence of GECA certification and will be accepted in lieu of actual copies of the GECA license agreement.
x |  |  |  | x | x |  | x | 2007-12-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 4 | Materials Calculators 'Manufacturer' refers to the final manufacturer that assembles the product, not all the manufacturers of individual components from raw materials (e.g., steel). If there are two primary manufacturers (e.g., one of the base and one of the tabletop), both would need to provide evidence that is required of the 'manufacturer'. To discourage the removal of new base building carpet installed prior to the tenancy fitout, such carpet can be deemed 'reused'. However, such a claim disqualifies the project from claiming Eco-5 'Shell and Core or Integrated Fitout', as that credits rewards a preferable environmental outcome, i.e. avoiding unnecessary installation in the first place.
x | x | x | [5 empty] | 2007-08-01 | Mat-0 | Mat-0 | Mat-0 |  | General | Technical Clarification | 5 | While the Credit Criteria states "shell and core OR integrated fitout", any combination of these is acceptable, i.e. areas delivered as shell-and-core and areas delivered as integrated fitout must jointly contribute the required proportion of the NLA.
x | x | x | [5 empty] | 2007-08-01 | Mat-0 | Mat-0 | Mat-0 |  | General | Technical Clarification | 6 | The installation of the raised floor system and the perimeter cell air conditioning displacement system is appropriate for Shell & Core project delivery as long as carpet tiles are not installed.
x | [7 empty] | 2008-07-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 7 | Modularity: The Green Star intent for ‘modularity’ is founded on the premise that the adjustment and replacement of the product is easy to manage. In the particular case of Flooring, for example, as a rule the GBCA does not consider any product greater than 1m2 in dimension to be modular. In other words, sixteen 1m rolls of sheet flooring do not meet the Green Star intent of ‘modularity’.
x |  |  |  | x | x |  | x | 2008-07-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 8 | Design for Disassembly: Documentation of ‘design for disassembly’ criteria in Green Star was generally intended for product streams containing distinct componentry (e.g. furniture, partitions, storage). The level of documentation required for flooring products does not apply to 'one-piece' materials. Sheet flooring is considered to be a one-piece material, and therefore cannot claim 'Design for Disassembly’ for the purposes of the Flooring Calculator in the Green Star - Office Interiors rating tool. Whilst some flooring products can be separated and their components downcycled or upcycled or reused, the processes which are required to do so are complex, and require specialist tools and processes. These are generally, but not necessarily, linked closely with product stewardship initiatives, which is a separate issue recognised in the Flooring Calculator.
x | [7 empty] | 2009-02-01 | Mat-0 |  |  |  | General | Technical Clarification | 9 | Correction: Mat-0 Technical Clarification No. 3, will be amended to the following: When submitting for Green Star Office Interiors v1 & v1.1, the following must be included: - A copy of the completed Calculator; - Receipts and/or information from the sub-contractor or supplier confirming that the fitout items were supplied and installed within the tenancy; and - The GECA Certificate to enable the Certified Assessors to identify a GECA certified product. This level of documentation is sufficient for GECA certified products ONLY. All other fitout items must be submitted as per the Green Star Technical Manual.
x | x | x | x | x | x | x | x | 2009-07-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General | Technical Clarification / CIR Ruling / Correction | 10 | For a product or material to be classified as ‘reused’ at least 80% by area, length, volume or mass, whichever is more appropriate (metric chosen must be justified) of the item must be retained; the rest can be refurbished or new, as in the case of new upholstery, painting or coating, etc.
x |  |  |  | x | x |  | x | 2009-07-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General | Technical Clarification / CIR Ruling / Correction | 11 | A new Materials Calculator Guide has been released for the tool. All projects registered after June 23rd,2009 must use this guide. Projects registered prior to this date can choose to use the guidance provided in the Technical Manual, or this guide. In order to simplify all materials calculators accross all tools, small changes have been made to how points are calculated. This change is minor and should not affect most projects. Projects must download updated excel tools from the website.
x | [6 empty] | x | 2009-10-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 12 | The final product’s (i.e. workstation, walls and partitions) onsite installer (i.e. carpenter or joiner etc) is not considered the manufacturer for the purpose of the Material Calculators. All the product elements from one or more supplier should be entered into one line of the Calculator, and inputs should reflect 'the weakest link', should there be a difference (e.g., durability should be assessed against the least durable of the components). Up to 10% by weight of a wall's component(s) may be disregarded for the process of documentation, for example aluminium lining and screws.
x |  |  |  | x | x |  | x | 2010-03-01 | Mat-0 |  |  | Mat-0 | General | Technical Clarification | 13 | Additional schemes have been recognised as environmentally innovative in this category. Please see: http://www.gbca.org.au/green-star/materials-category/product-and-forest-certification-schemes/1616.htm
x | x | x | x | x | x | x | x | 2010-12-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General | Withdrawn | 14 | Withdrawn 01-Jul-12 replaced by ruling Mat-0 # 18. In the 'Materials' category, 'As-Built Documentation' for several credits requires confirmation from a subcontractor, that a particular item or product was used on site. Confirmation of this information from the head contractor is also considered to be acceptable.
x | x | x | x | x | x | x | x | 2010-12-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | General | Technical Clarification | 15 | Durability' entries in the Material Calculator refer to the warranty of a whole product.
|  |  |  | x | x |  | x | 2010-12-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | Material Calculators | Technical Clarification | 17 | Product Stewardship - In a Design submission, In place of a signed contract submit an extract from the specification, stipulating that the items will be purchased under an agreement that includes a product stewardship contract.
x | x | x | x | x | x | x | x | 2012-08-01 | Mat-0 | Mat-0 | Mat-0 | Mat-0 | Material Calculators | Technical Clarification | 18 | For As Built projects, confirmation that a particular item or product was installed on site may be provided by any of the following: - subcontractor; or - head contractor; or - building owner; or - tenant.
x | x | x | x | x | x | x | x |  | Mat-9 | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage
x | x | [6 empty] | 2007-12-01 | Mat-9 | Mat-1 |  | Mat-1 | Recycling Waste Storage | Technical Clarification | 1 | The 'City of Sydney Code for Waste Handling in Building' (2004) has been replaced by 'Policy for Waste Minimisation in New Developments'. To demonstrate that the location and layout of the storage area is easily accessible by recycling collection vehicles, projects may still provide a letter from the recycling company (as stipulated in the Technical Manual), or demonstrate compliance with the 'Access' requirements of the following sections of the 'Policy for Waste Minimisation in New Developments': Section A, points A-12 through A-17, and Section C, points C6 and C7.
| x | x | [5 empty] | 2007-12-01 |  | Mat-1 | Mat-1 |  | Recycling Waste Storage | Technical Clarification | 2 | It is acceptable to meet the Credit Criteria of Mat-1 'Recycling Waste Storage' with more than one dedicated storage area. However, all storage areas dedicated to recycling must meet all the Credit Criteria and Additional Guidance requirements (such as location within 20m of a lift core) and be functional (e.g., an area may not be so small that it cannot house at least 3 standard bins as used in municipal waste collection). An area dedicated exclusively to storage of rubbish (non-recycling waste) should be excluded. In addition, where other uses (for base building projects) or tenants (for fitout projects) are present in the building, it must be clearly demonstrated that the office use of the recycling waste storage facilities is not compromised (e.g., how a proportion of facilities is dedicated for exclusive use of the project).
| x | x | x | x |  |  |  | 2008-08-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 3 | Additional criteria have been developed to clarify the meaning of “good access for all building occupants and for collection by recycling companies.” The Technical Manual makes the following reference: “The space needs to be placed so that it is within easy reach of office areas – i.e. within approximately 20m of the base of the lift core serving all floors.” Additionally, projects may claim the points if the Credit Criteria are met and the dedicated storage area for the separation and collection of office recyclables is located in the same level as the loading dock with a clearly marked, sign-posted, convenient and guaranteed access route within one of the following walking distances: - 20 metres of the exit used for recycling pick-up; OR - 20 metres of the lift core serving all floors; OR - 3m of the shortest route connecting the lift core serving all floors and the exit used for recycling pick-up.
| x | x | [5 empty] | 2008-10-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 4 | When calculating the required minimum area of recyclable storage space, projects must always round to the nearest and larger full metre. For example, for a project that has an nominated area of 750m2, the minimum recyclable storage space will be 8m2.
[8 empty] | 2008-09-01 |  |  |  | Mat-1 | Recycling Waste Storage | CIR Ruling | M1 | The Credit Interpretation Request to have recycling bins on each floor be deemed equivalent to general garbage and recycling ‘chutes’ is granted conditionally on the project’s ability to demonstrate that:  Recycling bins have been provided on each floor, either next to the general garbage chutes, or within 5 meters of the chute. A sign must indicate that the recycling bins are nearby.  The number of recycling bins is able to service the entire floor (the number of bins on each floor must be calculated as per the local authority’s guidelines. Where the guidelines do not exist, or the number of bins required per floor is less than one, at least one bin for each waste stream must be provided; and  Where the development has a loading dock from which the garbage will be picked up from, there is a centralised general garbage and recycling bin space which caters for all the garbage and recycling waste of the building.
[8 empty] | 2008-09-01 |  |  |  | Mat-1 | Recycling Waste Storage | CIR Ruling | M2 | The Credit Interpretation Request to exclude the project from having an onsite disposal and re-use of compost and green waste facilities because it is not practical in a high rise development is denied. The project has not proposed an alternative yet equivalent method. Please note that this feedback is acknowledged, and may be used to inform the Green Star - Multi Unit Residential v1 tool.
[8 empty] | 2008-10-01 |  |  |  | Mat-1 | Recycling Waste Storage | CIR Ruling | M3 | The sizing of the recycling waste storage for Green Star – Multi Unit Residential PILOT must meet the size requirements in table Mat-1.1 on page 237 of the Technical Manual for Green Star – Office v3. All credits are being reviewed before the release of Green Star – Multi Unit Residential v1, so please provide feedback and suggest alternative requirements if you feel that these sizing requirements needs to be revised.
| x | x | [5 empty] | 2008-12-01 | Mat-1 | Mat-1 | Mat-1 |  | Recycling Waste Storage | Technical Clarification | 5 | Where a project’s recycling waste storage facilities are further than the stipulated distance from the base of the lift core, projects will need to submit a CIR for consideration by the GBCA to justify the alternative distance.
|  |  | x | x | x | x | x | 2009-04-01 |  |  |  | Mat-1 | Recycling Waste Storage | Correction | 6 | The waste auditor must have a minimum of five years experience working in the commercial and industrial area, with specific experience in conducting commercial audits in line with guidelines issued by State/Territory waste authorities. • Australian Capital Territory: Department of Territory and Municipal Services (TAMS) • New South Wales: Department of Environment and Climate Change (DECC) • Northern Territory: Natural Resources, Environment, the Arts and Sport (NRETAS) • South Australia: Zero Waste SA • Tasmania: Department of Environment, Parks, Heritage and the Arts (DEPHA) • Victoria: Department of Sustainability and Environment (DSE)/Sustainability Victoria • Western Australia: Department of Environment and Conservation (DEC) • Queensland: Environmental Protection Agency (EPA) Compliance Requirements: The short report must include evidence of the waste auditor’s relevant professional experience (such as professional degree(s), list of previous waste audits and professional references).
[7 empty] | x | 2010-12-01 |  |  |  | Mat-1 | Recycling Waste Storage | Correction | 7 | The credit criteria in the technical manual describes five initiatives that can be implemented to meet the credit aims: 1. Dedicated Storage Areas 2. Convenience of Recycling 3.Waste Chutes 4. Compost Facilities 5. Facilities for Over-sized Household Items In fact, only four inititatives can be considered. 'Waste Chutes' is not a separate initiative. 'Waste Chutes', as defined here, is a way of facilitating 'Convenience of Recycling'.
|  |  | x | x |  |  |  | 2010-12-01 |  |  |  | Mat-1 | Recycling Waste Storage | Technical Clarification | 8 | The manual refers to: 'Policy for Waste Minimisation in New Developments (NSW 2004). The reference should be: 'Policy for Waste Minimisation in New Developments' - Council of the City of Sydney (2005).
x | [7 empty] | 2010-12-01 | Mat-9 |  |  |  | Recycling Waste Storage | Correction | 9 | A workstation consists of a work surface designed to accommodate one user. A workstation may include storage elements and screening devices. A workstation designed to accomodate three usres should be counted as three workstations.
|  |  | x | x | x | x |  | 2010-12-01 |  |  | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 10 | RABQSA Waste Auditor Certification is an acceptable qualification for a 'Waste Auditor' for the purposes of this credit. For Healthcare v1, other acceptable qualifications are described in the technical manual. For Education v1, other acceptable qualifications are described in Correction 6, April 2009.
[8 empty] | 2009-10-01 | Mat-9 | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | CIR Ruling | P | The Credit Interpretation Request to deem the location of the recyclable storage area as being within easy reach of office areas is granted conditionally. The project team must provide a short report of how the recyclable wastes will be transferred to this storage area and how facilities are designed to ensure that the recyclables can easily be transferred over this distance.
[8 empty] | 2009-10-01 | Mat-9 | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | CIR Ruling | P | The Credit Interpretation Request to deem DA Approval sufficient to confirm that the location and layout of the storage area is easily accessible by recycling vehicles is denied. Assessment of access via a DA approval is not considered equivalent to the methods of compliance identified by the technical manual. As the local council is acting as the commercial building recycling company in this case, a letter from Council confirming that the development facilitates easy access for Council collection vehicles would satisfy the requirements.
[8 empty] | 2009-10-01 | Mat-9 | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | CIR Ruling | P | The Credit Interpretation Request to deem the location of the recyclable storage area as being within easy reach of office areas is granted conditionally. The project team must provide a short report of how the recyclable wastes will be transferred to this storage area and how facilities are designed to ensure that the recyclables can easily be transferred over this distance.
| x | x |  | x | x | x | x | 2012-08-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 11 | It is acceptable for the recycling storage area to be adjacent to the general waste storage area, as long as the following can be demonstrated: - Clear separation must exist between the two storage areas. This can be through paint markings on the floor or a rail dividing the space. - Where these areas are designed to be in the same area, provide a drawing showing the layout of the bins clearly demonstrating adequate space for bin maneuverability for both recycling and waste bins.
| x | x | x | x | x | x | x | 2012-08-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 12 | It is acceptable to use a ramp where level change is necessary along the access route to the recycling waste storage. The gradient of the ramp must not exceed 1:8 (one meter in every eight metres).
| x | x | x | x | x | x | x | 2012-08-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 13 | The recycling waste storage and the loading dock can be located on different levels provided that they are connected with a goods lift.
|  | x | [5 empty] | 2012-08-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | Technical Clarification | 14 | The credit criteria requires project to comply with section C of the Policy for Waste Minimisation in New Developments (NSW, 2005). Points C6 and C7 of this document should not be included in the credit criteria as those are not related to recycling waste storage as adresssed by this credit.
x | [7 empty] | 2013-11-01 |  | Mat-1 | Mat-1 | Mat-1 | Recycling Waste Storage | CIR Ruling | 15 | Projects may use the following rates for the provision of recycling storage space: • 1m2 per 12 workstations where there is a fortnightly collection service in place; • 1m2 per 24 workstations where there is a weekly collection service in place; and • 1m2 per 120 workstations where there is a daily recycling collection service in place. All documentation must be submitted as per the Compliance Requirements.
| x | x | x | x | x | x | x |  |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use / Re-use of Façade
| x | x | x | x | x |  | x | 2006-01-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use / Re-use of Façade | Technical Clarification | 1 | To demonstrate the proportion of total façade being reused you need to demonstrate by area the proportion of reused and new. Where there is a reused portion, only 20% of the materials used within the reused portion can be new (i.e. new shading elements etc). Hence, to claim this Credit a project must demonstrate that the new materials added to the reused portion equate to less than 20% of the total materials in the reused portion by mass.
| x | x | x | x | x |  | x | 2006-01-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use / Re-use of Façade | Technical Clarification | 2 | If no new materials are added to the reused portion, this needs to be clearly identified and a demonstration of mass is not necessary. It is recommended that you speak to your Façade Consultant regarding estimating the mass of existing façade. The Certified Assessor(s) will be looking for detailed calculations and justification of assumptions of all existing materials that are to be maintained in the refurbishment.
| x | [6 empty] | 2006-06-01 |  | Mat-2 |  |  | Building Re-use / Re-use of Façade | Technical Clarification | 3 | If the buildings demolished as a consequence of the development that seeks Green Star assessment extend beyond the site boundary, then their total area must be used in calculations for these credits.
| x | x | x | x |  |  |  | 2007-12-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use / Re-use of Façade | Technical Clarification | 4 | This Credit is ‘Not Applicable’ (na) for Greenfield sites (as per the Credit Criteria) or for sites on which no buildings existed at the time of purchase of the site (please provide evidence of site purchase and site drawings or aerial photographs dated at or before the date of the site purchase, with all existing structures clearly identified).
| x | x | [5 empty] | 2008-03-01 |  | Mat-2 | Mat-2 |  | Building Re-use / Re-use of Façade | Withdrawn | 5 | For Office v2 projects, see Correction Mat-2/7 for more information For Office v3 projects, see Correction Mat-2/8 for more information The ‘Not Applicable’ (na) clause within the Technical Manual should read as follows: “Where the site is a Greenfield site…. or contained no buildings at the time of purchase… or the total GFA of the original building(s) is less than 20% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score.”
| x | [6 empty] | 2008-09-01 |  | Mat-2 |  |  | Building Re-use / Re-use of Façade | Technical Clarification | 6 | For a greenfield site, an aerial photograph of the site, taken at or prior to the time of site purchase, is acceptable documentation of the site’s original condition to meet the ‘NA’ clause in the Credit Criteria.
| x | [6 empty] | 2008-03-01 |  | Mat-2 | Mat-2 |  | Building Re-use / Re-use of Façade | Correction | 7 | The ‘Not Applicable’ (na) clause within the Technical Manual should read as follows: “Where the site is a Greenfield site or contained no buildings at the time of purchase or the total GFA of the original building(s) is less than 30% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score.”
|  | x | [5 empty] | 2008-03-01 |  |  | Mat-2 |  | Building Re-use / Re-use of Façade | Correction | 8 | The ‘Not Applicable’ (na) clause within the Technical Manual should read as follows: “Where the site is a Greenfield site or contained no buildings at the time of purchase or the total GFA of the original building(s) is less than 20% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score.”
| X | [6 empty] | 2009-07-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use / Re-use of Façade | Technical Clarification | 9 | For refurbishment rpojects, rather than provide new drawings of the façade, the project can provide archival ‘as-built’ drawings marked up to show the location and area of the reused façade, as well as a statement from the Architect confirming that all of the façade has been retained. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where facade or structure are being reused: * Tender drawings of the new building * Extract(s) from the specification Where facade or structure are being reused, the following documentation, As-built drawings of original building(s), can be substituted with the following: * Original building documentation; or * Site survey of existing building; or * Demolition plans; Provided that these contain the same level of information as that which is required in the Technical Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use | Documentation (As Built) | C | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: Where facade or structure are being reused * As Built drawings of the new building Where facade or structure are being reused, the following documentation, As-built drawings of original building(s), can be substituted with the following: * Original building documentation; or * Site survey of existing building; or * Demolition plans; Provided that these contain the same level of information as that required in the Technical Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use | Documentation (As Built) | D | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the General section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use | Documentation | E | Where the credit is claimed as 'Not Applicable', regardless of whether the site contained no buildings at the time of purchase, or whether the exiting building(s)’ GFA is less than 20% of the new building(s)' GFA, the following documentation must be submitted. * Short Report prepared by a suitably qualified professional that describes how the Credit Criteria have been met by: - Providing calculations and a complete area schedule demonstrating that the GFA of the original building(s) is less than 20% of the GFA of the building replacing them, referencing documentation from original buildings; OR - Stating that no buildings existed on the site at the time of purchase.
|  | x | x | x | x | x | x | 2013-11-01 |  | Mat-2 | Mat-2 | Mat-2 | Building Re-use | Documentation (As Built) | F | The credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x |  |  | Mat-3 | Mat-2 | Mat-2 | Building Re-use / Re-use of Structure
| x | [6 empty] | 2006-01-01 |  | Mat-3 |  |  | Building Re-use / Re-use of Structure | Technical Clarification | 1 | If the buildings demolished as a consequence of the development that seeks Green Star assessment extend beyond the site boundary, then their total area must be used in calculations for these credits.
| x | [6 empty] | 2006-01-01 |  | Mat-3 |  |  | Building Re-use / Re-use of Structure | Technical Clarification | 2 | These credits are ‘Not Applicable’ (na) for Greenfield sites (as per the Credit Criteria) or for sites on which no buildings existed at the time of purchase of the site (please provide evidence of site purchase and site drawings or aerial photographs dated at or before the date of the site purchase, with all existing structures clearly identified).
| x | [6 empty] | 2008-01-01 |  | Mat-3 |  |  | Building Re-use / Re-use of Structure | Withdrawn | 3 | For Office v2 projects, see Correction Mat-3/6 for more information The ‘Not Applicable’ clause within the Technical Manual should read as follows: “If the site is a Greenfield site…. or contained no buildings at the time of purchase… or the total floor area of existing buildings demolished on-site is less than 30% of the NLA of the new building then the credit is ‘Not Applicable’ and is excluded from the points available to calculate the Materials Category Score.”
| x | [6 empty] | 2006-01-01 |  | Mat-3 |  |  | Building Re-use / Re-use of Structure | Technical Clarification | 4 | The project will need the following figures in order to perform the required calculations: FIGURE 1: Entire gross volume of existing building prior to demolition ("existing structure"); FIGURE 2: Entire gross volume of existing building after demolition ("re-used structure'); and FIGURE 3: Entire gross volume of completed building (including the re-used structure and new building structure). The project must first determine if the re-used structure (FIGURE 2) comprises at least 50% of the completed building (figure 3). Once this has been established, the project will be required to do the following calculations to determine if they are eligible for any points. Compare the "re-used structure" (FIGURE 2) to the "existing structure" (FIGURE 1) to determine what percentage of the "existing structure" is being retained. This percentage is used to determine how many points the project is entitled to.
| x | [6 empty] | 2008-09-01 |  | Mat-3 |  |  | Building Re-use / Re-use of Structure | CIR Ruling | 5 | For a greenfield site, an aerial photograph of the site, taken at or prior to the time of site purchase, is acceptable documentation of the site’s original condition to meet the ‘NA’ clause in the Credit Criteria.
[8 empty] | 2008-10-01 |  |  |  | Mat-2 | Building Re-use | CIR Ruling | M1 | The Credit Interpretation Request to deem the credit N/A where all buildings in a site were legally required to be demolished is granted conditionally on the project’s ability to demonstrate, via a short letter from the building owner, that such was a requirement from a regulatory body.
| x | [6 empty] | 2008-01-01 |  | Mat-3 | Mat-2 |  | Building Re-use / Re-use of Structure | Correction | 6 | The ‘Not Applicable’ (na) clause within the Technical Manual should read as follows: “Where the site is a Greenfield site or contained no buildings at the time of purchase or the total GFA of the original building(s) is less than 30% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score.”
|  | x | [5 empty] | 2008-01-01 |  |  | Mat-2 |  | Building Re-use / Re-use of Structure | Correction | 7 | The ‘Not Applicable’ (na) clause within the Technical Manual should read as follows: “Where the site is a Greenfield site or contained no buildings at the time of purchase or the total GFA of the original building(s) is less than 20% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score.”
|  | x | x | x | x | x | x |  |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials
[7 empty] | x | 2009-05-01 |  |  |  | Mat-3 | General | Technical Clarification | 1 | The word 'and' in the ‘recycled-content’ and ‘reused products and materials’ components of this credit shall be interpreted as AND/OR. This means you only need to comply with one of the criteria. Therefore, materials selected for building construction representing at least 1% of the project’s total contract value should EITHER have a post-consumer recycled content of at least 20% OR be reused. You may demonstrate that both criteria are achieved, however this is not a requirement of the Credit Criteria. Please ensure that any recycled content being claimed is based on percentage of post-consumer recycled content and not post-industrial recycled content.
|  | x | x | x | x | x | x | 2011-01-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Correction | 2 | This credit addresses permanent features of the building. It does not take into account the tools or temporary implements used during construction, nor does it include products or materials used on a temporary basis in the construction of the project. Hoardings, overhead protection systems, formwork, temporary electrical and plumbing equipment are not considered. Non-fixed appliances, stationery and other consumables cannot be counted as reused or recycled in this credit.
|  | x | x | x | x | x | x | 2011-01-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Correction | 3 | The monetary value of reused materials and products can be calculated as follows: -The purchase price of the same materials or products when new; OR -The purchase price of similar materials or products.
|  | x | x | x | x | x | x | 2011-01-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Technical Clarification | 4 | For any project that uses the PVC credit released on April 7, 2010: - Any reused PVC products are no longer part of the scope of the PVC credit. - Reused PVC products are now considered to be part of the scope of 'reused' materials for the credit 'Reused Materials' or Recycled Content & Re-used Products and Materials'.
|  | x |  | x | x | x | x | 2012-08-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Technical Clarification | 5 | Written confirmation of the contract value by a qualified quantity surveyor can be submitted in place of extracts from the contract.
|  | x | [5 empty] | 2012-08-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Correction | 6 | This credit has been changed as follows: One point is awarded where at least 2% of the project's total contract value is represented by: - Re-used products/materials; OR - Post-consumer recycled content of at least 50%. This credit excludes materials specifically addressed by other credits (i.e. steel, concrete, PVC and timber); neither does it address the reuse of the original building(s) on site (addressed in Mat-2 'Building Reuse') NB: Post-consumer recycled content refers to the product composition that contains materials diverted from the product user's waste stream. This excludes re-utilisation of materials such as rework, regrind or scrap generated in a process and capable of being reclaimed within the same process that generated it.
|  | x | x | x | x | x | x | 2012-08-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Technical Clarification | 7 | For As-Built projects: As evidence of recycled content project teams may provide: - A Manufacturer's Data Sheet specifying the post-consumer recycled content; or - A certificate based on an ISO 14044 compliant Life Cycle Analysis issued by a GBCA recognised product certification scheme (where this certificate reports on the post-consumer recycled content of the material); or - An ISO 14025/EN 15804 compliant Environmental Product Declaration issued by a GBCA recognised product certification scheme (where this declaration reports on the post-consumer recycled content of the material). Ecospecifier's Global GreenTag LCARate Scheme satisfies the above requirement.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Extract(s) from specification(s) * Extract(s) from schedule(s) Projects must submit the following documentation instead: * Extract(s) from tender documentation where the reused products and materials in the project as well as the associated quantities of these materials are stipulated. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Mat-3 | Mat-3 | Mat-3 | Reused Materials / Recycled Content & Re-used Products & Materials | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Extract(s) from the issued contract(s) Projects must submit the following documentation instead: * Extract(s) from As Built documentation where the reused products and materials in the project as well as the associated quantities of these materials are stipulated. All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x |  |  |  | x | x |  |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout
| x | x |  |  |  | x | x | 2007-08-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | Technical Clarification | 1 | While the Credit Criteria states "shell and core OR integrated fitout', any combination of these is acceptable, i.e. areas delivered as shell-and-core and areas delivered as integrated fitout must jointly contribute the required proportion of the NLA.
| x | [6 empty] | 2007-08-01 |  | Mat-4 |  |  | Shell and Core or Integrated Fitout | Withdrawn | 2 | For more information, please see the Green Star As Built Guidelines for more information: http://www.gbca.org.au/technical-clarifications-cir-rulings/green-star-as-built-guidelines/1876.htm For projects that are delivered as shell-and-core, the GBCA will be issuing submission guidelines that will illustrate how this form of project delivery will affect the projects' compliance with affected credits.
| x | x |  |  |  | x | x | 2007-08-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | CIR Ruling | 3 | The installation of the raised floor system and the perimeter cell air conditioning displacement system is appropriate for Shell & Core project delivery as long as carpet tiles are not installed.
[8 empty] | 2008-10-01 |  |  |  | Mat-11 | Shell and Core | CIR Ruling | M1 | The CIR to deem Integrated Fitout equivalent to Shell & Core is granted. Therefore the point can be claimed.
| x | x | [5 empty] | 2008-12-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | Technical Clarification | 4 | Emergency or safety lighting, and the relevant fire suppression systems, that have been installed throughout the general office area, as required by the Building Code of Australia, is excluded from this Credit. Projects must clearly indicate in the submitted drawings that this is the case. The Certified Assessors will look to ensure that these installed services cannot be used for the purposes of general office use.
| x | x | [5 empty] | 2008-12-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | Technical Clarification | 5 | Where the occupancy certificate does not show the required information by this credit or where the occupancy certificate is not available, it is acceptable for the project to provide letters from the tenant and owner, as follows: - A Letter from tenant outlining the tenancy requirements; and - A Letter from owner confirming that base building can adequately provide for the tenant requirements.
| x | x | [5 empty] | 2009-04-01 |  | Mat-4 |  |  | Shell and Core or Integrated Fitout | Technical Clarification | 6 | The Green Star As Built Guidelines have been released. For more information, please see http://www.gbca.org.au/technical-clarifications-cir-rulings/green-star-as-built-guidelines/1876.htm
|  | x |  |  |  | x | x | 2009-03-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where the project has shell and core elements: * Extract(s) from the specification(s) * Tender drawings Where the project has integrated fitout elements: *Tender drawings. *Confirmation(s) from the tenant(s). All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x |  |  |  | x | x | 2009-03-01 |  | Mat-4 | Mat-4 | Mat-10 | Shell and Core or Integrated Fitout | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: Where the project has shell and core elements: * Occupancy Certificate Where the project has integrated fitout elements: * Project Timeline * Confirmation from the contractor * Occupancy Certificate All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | x | x | x | x |  |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete
| x x x | x | x | x | x | x | x | 2012-07-01 |  | Mat-5 | Mat-5 | Mat-4 | Please note there is a revised version of this credit called 'Concrete' which was released on 15/05/2012. If your project was registered after 01/07/2012, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/materials-category/revised-green-star-concrete-credit/34008.htm
| x | [6 empty] | 2006-06-01 |  | Mat-5 |  |  | Concrete / Recycled Content of Concrete | Technical Clarification | 1 | Use of recycled aggregate and cement replacement are separate initiatives, in other words, it is not a prerequisite to claim recycled aggregate in order to claim cement replacement.
| x | x | x | x | x | x | x | 2007-08-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem "aggregate from waste rock returned from sites" equivalent to "recycled aggregate derived from crushed concrete", due to the stated absence of aggregate recycled from concrete in Melbourne, is denied. The very aim of the Green Star tools is to change standard practices in the industry towards more sustainable and recycled methods - GBCA research has identified aggregate recycled from concrete and suppliers of this material within the state of Victoria.
| x | [6 empty] | 2007-12-01 |  | Mat-5 |  |  | Concrete / Recycled Content of Concrete | Technical Clarification | 3 | With the Compliance Requirements, the third bullet point is only applicable to projects where the second bullet point is ‘True’. So ALL projects must submit the evidence within the first bullet point, but only some projects have to submit the evidence within the third bullet point as well.
| x | x | x | x | x | x | x | 2008-08-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Technical Clarification | 4 | This credit deals with the percentage of post-consumer recycled content in the aggregate used in concrete during project’s construction. It is acceptable to calculate the required 20% against the total volume of aggregates used across the project, in all concrete mixes. The recycled content of concrete can therefore be calculated across the entire concrete use in the building.
| x | x | x | x | x | x | x | 2008-10-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Technical Clarification | 5 | Slag is a by product of the manufacture of steel. Ground Granulated Blast Furnace Slag (GGBFS) is slag ground to cement fitness and is a cementitious binder.
[8 empty] | 2009-10-01 |  |  |  | Oct-08 | Concrete / Recycled Content of Concrete | Withdrawn | 6 | This clarification was originally posted in Oct-08. See TC No. 7 for more information. Slag aggregate is classified as an industrial waste product and can be used as an aggregate substitute for purposes of this credit.
| x | x | x | x | x | x | x | 2009-10-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Withdrawn | 7 | The following clarification has been withdrawn. Please see Technical Clarification No. XX for more information (originally posted on Jan-07) The Definition of recycled aggregate is being expanded and clarified to include the following: Aggregates derived from the processing of materials previously used in a product and/or aggregates from construction that would otherwise be put into landfill. Common types are as follows: Recycled concrete aggregates — produced by the reclamation, crushing and screening of demolition concrete waste, AND, slag agreggate which is an industrial waste product. Reclaimed aggregates — Produced from unused fresh concrete returned to its manufacturer in a state such that separation of the aggregates from the cement paste is still possible by washing and or screening, AND produced from crushing selected surface rock from excavation works associated with building construction.
| x | x | x | x | x | x | x | 2011-01-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Correction | 8 | For the purpose of this credit, recycled aggregate is defined follows: Aggregates derived from the processing of materials previously used in a product; and/or Aggregates from construction that would otherwise be put into landfill. Common types are as follows: Recycled concrete aggregates • Aggregates produced by the reclamation, crushing and screening of demolition concrete waste; and • Slag aggregate which is an industrial waste product. Reclaimed aggregates • Aggregates produced from unused fresh concrete returned to its manufacturer in a state such that separation of the aggregates from the cement paste is still possible by washing and or screening; and • Aggregates produced from crushing selected surface rock from excavation works associated with building construction. Documentation: Design: • As per the current credit. As Built: • Confirmation from the concrete supplier of the type of aggregate provided to the project; and • Confirmation from the contractor that this aggregate was used on the project.
|  | x | x | x | x | x | x | 2011-01-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Technical Clarification | 9 | For a Design rating, the concrete technologist role can be fulfilled by the structural engineer. For an As Built rating, the concrete technologist role can NOT be fulfilled by the structural engineer.
| x | [6 empty] | 2012-08-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Technical Clarification | 10 | Project teams are not required to submit any documentation demonstrating that concrete makes up more than 1% of the contract value to claim the points in Mat-5 ‘Recycled Content of Structural Concrete’ credit, such documentation is only required when the credit is claimed as ‘Not applicable’.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: To demonstrate replacement of Portland Cement: * Quantity Surveyor report * Extract(s) from the main building contract. Where credit is claimed as 'Not Applicable': * Extract(s) from the main building contract. Projects must submit the following documentation instead: * Short Report summarizing: - To demonstrate replacement of Portland Cement, the findings of the Concrete Technologist Report, OR; - Where the credit is claimed as 'Not Applicable', stating that the quantities of the total material value of the new concrete as a proportion of the project's total value represents less than 1% of the project's contract value. All other documentation must be provided as per the Technical Manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Correction | B | The following documentation is no longer required for Green Star - As Built submissions for this credit: To demonstrate replacement of Portland Cement: * Quantity Surveyor Report * Extract(s) from the contract * Confirmation from the contractor. Where credit is claimed as 'Not Applicable': * Extract(s) from the contract Projects must submit a report by a suitable concrete technologist. For projects applying to claim this credit, the report must demonstrate replacement of Portland Cement. Where the credit is claimed to be 'Not Applicable', a Concrete Technologist's statement must be submitted. This must state that the quantities of the total material value of the new concrete represents less than 1% of the project's total contract value. All other documentation must be provided as per the Technical Manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-5 | Mat-5 | Mat-4 | Concrete / Recycled Content of Concrete | Documentation | C | Where the credit is claimed as 'Not Applicable', projects may provide, in place of the Quantity Surveyor report, either a Report from a Structural Engineer, or a report from the Cost Planner, stating that the quantities of the total material value of the new concrete as a proportion of the project's total value represents less than 1% of the project's contract value.
| x | x | x | x | x | x | x |  |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel
|  | x x x | x | x | x |  | x | 2010-04-30 |  | Mat-6 | Mat-6 | Mat-5 | Please note there is a revised version of this credit called 'Steel' which was released on 29/04/2010. If your project was registered after 29/04/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/materials-category/revised-green-star-steel-credit/1825.htm
| x | [6 empty] | 2007-12-01 |  | Mat-6 |  |  | Steel / Recycled Content of Steel | Technical Clarification | 1 | While the Credit Criteria refers to ‘all steel’, this credit addresses structural applications of steel only, i.e. structural and reinforcing steel.
| x | x | x | x | x | x | x | 2007-12-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Technical Clarification | 2 | It must be clear that the evidence accounts for all uses of the relevant material in the project, i.e. via using ‘all’ in the specification or, where appropriate, providing a summary table listing all uses and the attributes of the material(s) used.
| x | x | x | x | x | x | x | 2009-07-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Withdrawn | 3 | This clarification was modified to add additional suitably qualified consultants. It now reads. The Compliance Requirements state that a copy of the design schedule needs to be an official document appended to the specification. Where the copy of the design schedule is not appended to the specification, it can instead be provided on letterhead and signed by the relevant Quantity Surveyor, Cost Planner, or Structural Engineer.
| x | x | x | x | x | x | x | 2007-12-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Technical Clarification | 4 | All steel used within the building structure is addressed by this Credit, including all concrete reinforcement steel and structural steel. This includes, but is not limited to, hot rolled beams, columns, angles, mullions, and reinforcement as well as cold formed products such as purlins, girts, cladding and profiled steel decking.
| x | x | x | x | x | x | x | 2009-05-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Correction | 5 | This correction applies to all projects registered after this date. Projects registered prior to this date can choose to submit as per the technical manual or as per this correction. The compliance requirements for this credit state that “the evidence of recycled content refers to minimum, not average proportions of post-consumer content.” This statement is being reviewed and clarified. If the exact percentage of post-consumer recycled content of each steel product cannot be determined, average percentage of post-consumer recycled content of that type of steel product from that manufacturer will be accepted. Confirmation from the supplier of the post-consumer recycled steel content is required.
| x | x | x | x | x | x | x | 2009-05-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Correction | 6 | This correction applies to all projects registered after this date. Projects registered prior to this date can choose to submit as per the technical manual or as per this correction. There are two methodologies for demonstrating compliance: 1) Product by product The average post-consumer recycled content of steel in a project can be demonstrated on a product by product basis. The post-consumer recycled content of each product must be confirmed from the supplier. The percentage (by mass) of the products that meet the 50% post-consumer recycled content criteria should then be calculated. This percentage is then compared to the Credit criteria to determine how many Green Star points are awarded.
| x | x | x | x | x | x | x | 2009-05-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Correction | 6 | 2) Overall percentage The average post-consumer recycled content of steel in a project can be demonstrated through calculating the percentage (by mass) of post-consumer recycled steel used in the project. The overall percentage must be calcuated using the following method: 1. Calculate the mass of post-consumer recycled content used in the project 2. Calculate the percentage (by mass) of all steel that is post-consumer recycled content 3. Compare the percentage to the Credit criteria to determine how many points can be claimed, as follows; A. One point can be claimed when the overall percentage of recycled content is 30% or more. This is deemed to be equivalent to 60% of the steel in the project having a recycled content of 50%. B. Two points can be claimed when the overall percentage of recycled content is 45% or more. This is deemed to be equivalent to 90% of the steel in the project having a recycled content of 50%. An example of how the two different calculation methodologies can be found in the 'Steel Calculation' tab within this document
| x | [6 empty] | 2011-01-01 |  | Mat-6 |  |  | Steel / Recycled Content of Steel | Correction | 7 | This credit only assesses steel used in the building structure. Steel used in mechanical services equipment or hydraulic equipment, must be excluded from this credit.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where the project is claiming the use of reused or recycled steel: * Extract(s) from contract. * Quantity Surveyor report. * Steel Design Schedule Where credit is claimed as 'Not Applicable': * Extract(s) from the main building contract. Projects must submit the following documentation instead: Short Report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Identifying the total amount (by mass) of steel used within the building structure; - Identifying all of the applications of steel installed within the building structure; - Identifying the product used for each type of application; - Identifying the total amount (by mass) of steel used for each application within the building structure; - Referencing the quantity surveyor estimation of the total mass of steel in the building’s structure; and - Demonstrating via a summary table (and calculations wherever relevant) that the steel with confirmed post-consumer recycled content jointly accounts for the stipulated proportion of steel in the project. - If steel was supplied for uses outside the building structure, these uses must be clearly identified and excluded from the calculations. -OR- - Where the credit is claimed as 'Not Applicable', stating that the quantities of the total material value of the new steel as a proportion of the project's total value represents less than 1% of the project's contract value. All other documentation must be provided as per the technical manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Quantity Surveyor Report * Extract(s) from the contract * Confirmation from the contractor. Where credit is claimed as 'Not Applicable': * Extract(s) from the contract Projects must submit the following documentation instead: * Short Report Short Report prepared by a suitable professional that describes how the Credit Criteria have been met by: - Identifying the total amount (by mass) of steel used within the building structure; - Identifying all of the applications of steel installed within the building structure; - Identifying the product used for each type of application; - Identifying the total amount (by mass) of steel used for each application within the building structure; - Referencing the quantity surveyor estimation of the total mass of steel in the building’s structure, as well as supplier and contractor evidence of the post-consumer content of the steel used; and - Demonstrating via a summary table (and calculations wherever relevant) that the steel with confirmed post-consumer content jointly accounts for the stipulated proportion of steel in the project. - If steel was supplied for uses outside the building structure, these uses must be clearly identified and excluded from the calculations. -OR- - Where the credit is claimed as 'Not Applicable', that the stating that the quantities of the total material value of the new steel as a proportion of the project's total value represents less than 1% of the project's contract value. All other documentation must be provided as per the technical manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
|  | x | x | x | x | x | x | 2009-03-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Documentation | C | Where the credit is claimed as 'Not Applicable', projects may provide, in place of the Quantity Surveyor report, or a Report from a Structural Engineer, or a report from the cost planner, stating that the quantities of the total material value of the new concrete as a proportion of the project's total value represents less than 1% of the project's contract value.
| x | x | x | x | x | x | x | 2010-05-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Correction | 7 | A new revised Steel credit was released on April 29th, 2010. This follows a detailed review of the GBCA's Steel credit, conducted by an independent Steel Expert Reference Panel. Projects that register after April 29th, 2010 must use the revised version of the credit. Projects registered prior to this date have the option of continuing with the credit found in the Technical Manual, or using this revised version. Where projects registered prior to this date choose to use the revised version, this must be indicated on the cover page of this credit in their submission. To download this credit, please follow the link below, or click on this cell: http://www.gbca.org.au/green-star/materials-category/revised-green-star-steel-credit/1825.htm Prior Technical Clarifications for Mat-6 (Office v2 and Office v3) and Mat-5 (All other tools), do not apply to this credit.
| x | [6 empty] | 2012-08-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel | Technical Clarification | 8 | Project teams are not required to submit any documentation demonstrating that steel makes up more than 1% of the contract value to claim the points in the Mat-6 ‘Recycled Content of Structural Steel’ credit, such documentation is only required when the credit is claimed as ‘Not applicable’.
| x | x | x | x | x | x | x | 2013-11-01 |  | Mat-6 | Mat-6 | Mat-5 | Steel (April 2010) | Technical Clarification | 9 | Reinforcing steel includes reinforcing bar and mesh used in concrete reinforcement in the building structure. This includes steel in situ, stressed, and pre-cast concrete applications. For the purposes of this credit post tensioning tendons are not considered to be reinforcing steel and are therefore excluded from the scope of this credit.
x | x | x | x | x | x | x | x |  | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation
x x x |  | x | x | x | x |  | x | 2010-04-07 |  | Mat-7 | Mat-7 | Mat-6 | Please note there is a revised version of this credit called 'PVC' which was released on 7/04/2010. If your project was registered after 07/04/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/materials-category/revised-green-star-pvc-credit/2716.htm
| x | [6 empty] | 2007-08-01 |  | Mat-7 |  |  | PVC Minimisation | Technical Clarification | 1 | For refurbished buildings, existing PVC materials that are not being replaced are excluded from the cost calculations.
x | x | x | x | x | x | x | x | 2007-12-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Technical Clarification | 2 | If specified cabling has PVC sheathing but not PVC insulation, the submission must include documentation by the manufacturer to justify the reduction in PVC through avoidance of PVC insulation. The same logic would hold true for other composite products commonly including PVC.
x | x | x | x | x | x | x | x | 2007-12-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Technical Clarification | 3 | It must be clear that the evidence accounts for all uses of the relevant material in the project, i.e. through using the word ‘all’ in the specification or, where appropriate, providing a summary table listing all uses and the attributes of the material(s) used.
x |  |  | x | x | x | x | x | 2009-10-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Withdrawn | 4 | Originalle posted in Jun-08. See TC No. 7 for more information. CIR Ruling: The Credit Interpretation Request (CIR) to substitute the provision of cost estimates by a Qualified Quantity Surveyor, as required by the Technical Manual, with the actual costs provided by the contractors working on the project is granted on the basis that these costs reflect the true and actual costs of the materials, and reflect the actual finally-designed material quantities required for the project. However, as this credit is based on the estimated costs of uninstalled PVC items, where these are provided by the sub-contractor, they must be verified by a qualified Quantity Surveyor. The provision of the actual costs for a Green Star – Office As Built v2 submission does not remove the requirement to provide the documentation stated within the Compliance Requirements of the Credit.
| x | [6 empty] | 2008-09-01 |  | Mat-7 |  |  | PVC Minimisation | CIR Ruling | 5 | CIR Ruling: The Credit Interpretation Request (CIR) to exclude the communications cabling, electrical submains cabling and hydraulic pipework that will be installed as part of the integrated fitout from the calculations of the Mat-7 ‘PVC Minimisation’ credit is denied. These items are considered base building items regardless of whether they are installed during the integrated fitout process.
x | [7 empty] | 2008-07-01 | Mat-10 |  |  |  | PVC Minimisation | Technical Clarification | 6 | Base Building-installed PVC items, such as electrical cabling or piping, must not be included in the calculation for this credit, as those elements are considered part of the base building system. However, where one or both of the following are true, the PVC content must be considered as part of the fitout and included in the calculation; - Where the tenant moves into a space, and makes any additions or modifications to the installed PVC components during the fit out process; - Where the space is an integrated fitout, and the space is being rated for a Green Star – Office Interiors v1.1 rating.
x | x | x | x | x | x | x | x | 2009-10-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | CIR Ruling | 7 | Projects may choose to provide actual costs (provided by the contractors working on the project) in place of QS evidence. In order for this alternative methodology to be deemed acceptable, please ensure that these costs reflect the true and actual costs of the materials, (excluding labour and markups) and reflect the actual final-designed material quantities required for the project. As this credit is based on the estimated costs of uninstalled PVC items, where these are provided by the sub-contractor, they must be verified by a qualified Quantity Surveyor.
[8 empty] | 2009-10-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Correction | 8 | The PVC Reference Case Table that is linked to this technical clarification supersedes the guidance related to the benchmark percentage costs of PVC in the PVC reference cases provided in all tools. Projects register after xx/2009 must comply with this correction. All projects registered before this date have the following options: 1) Use the table 'PVC Reference Case' as per this technical clarification; or 2) Use the tables in the current Technical Manual. Project teams cannot combine elements from both options to support their submission.
[8 empty] | 2009-10-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Technical Clarification | 9 | The percentage cost of post consumer recycled PVC content in a product may be deducted from the total percentage cost of PVC in that product. For example: 1) Pipe - if the benchmark percentage cost of PVC in PVC pipe is 100% but the DWV pipe specified in the project uses PVC DWV pipe that contains 25% post consumer recycled PVC, then the benchmark percentage cost of PVC for the DWV pipe line item may be reduced to 75%. 2) Resilient Tile - if the benchmark percentage cost of PVC in a resilient tile is 10% but the resilient tile specified in the project is a PVC tile that contains 50% post consumer recycled PVC, then the benchmark percentage cost of PVC for the resilient tile line item may be reduced to 5%. Confirmation from the supplier (i.e. independent verification) must be provided to evidence the reduced percentage cost of PVC derived from post consumer recycled PVC content. Independent verification of the percentage of post consumer recycled PVC content in products will only be accepted from auditing bodies operating in conformance with ISO 17011:2004 ‘Conformity Assessment – General Requirements for Accreditation Bodies Accrediting Conformity Assessment Bodies’ or equivalent (e.g. JAS/ANZ accredited certification bodies).
x | x | x | x | x | x | x | x | 2010-05-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC | Correction | 10 | The GBCA released a revised Green Star ‘PVC’ credit on 7 April 2010. This follows an extensive 18-month review of the GBCA's previous Green Star ‘PVC minimisation’ credit. Under the revised Green Star ‘PVC’ credit, projects can claim two points towards their Green Star rating if the project’s flooring and resilient wall coverings, cable, pipe and conduit - which together account for the majority of PVC use in buildings - meet the GBCA's Best Practice Guidelines. See: http://www.gbca.org.au/green-star/materials-category/revised-green-star-pvc-credit/2716.htm for more information. Prior Technical Clarifications for Mat-11 (Office Interiors), Mat-8 (Office v2 and Office v3) and Mat-7 (All other tools), do not apply to the newly revised credit.
x | x | x | x | x | x | x | x | 2010-05-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC | Correction | 11 | Within the revised Green Star ‘PVC’ credit, PVC product manufacturers must demonstrate that their product meets the requirements of the ‘Best Practice Guidelines for PVC in the Built Environment’. This requires an independent audit as outlined in the ‘Verification Guidance Document’ (see Additional Guidance note). This ‘Verification Guidance Document’ is still under development. It is expected to be released by October 2010. Until this document is released, the ‘Evidence of Independent Verification’ requirement is replaced with the following document: Manufacturers’ Declaration Compliance of a PVC product to the Best Practice Guidelines shall be demonstrated by providing a manufacturer’s declaration. The declaration must: 1) Be provided on an official company letterhead; 2) Be signed by a company director; 3) State that the product supply chain (i.e. pipe, conduit, flooring, resilient wall coverings or cable insulation) supplied to the project is compliant with the requirements of sections 7.1 to 7.3 of the Literature Review and Best Practice Guidelines for the Life Cycle of PVC Building Products document, found in the GBCA website. 4) State that the company understands that the PVC Green Star credit requires verification of compliance to the Best Practice Guidelines for PVC in the Built Environment; and that it is commited to provide this verification by an independent body as soon as the Verification Guidance Document is released. Note: This clarification shall expire three months from the release of the Verification Guidance Document. Further clarifications related to the date of the release of the document will be posted here.
x | x | x | x | x | x | x | x | 2011-01-01 | Mat-10 |  |  |  | PVC Minimisation | Technical Clarification | 12 | PVC items that are re-used, from the project site or another site, must not be included in calculations for this credit.
x | x | x | x | x | x | x | x | 2011-01-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation/PVC | Technical Clarification | 13 | All Green Star projects registered on or after April 7th 2010 must use the 'PVC' credit, any earlier credits relating to PVC are not applicable.
x | x | x | x | x | x | x | x | 2011-01-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC Minimisation | Credit Interpretation Request | 14 | A Quantity Surveyor can provide the actual cost in place of the contractor or supplier.
x | x | x | x | x | x | x | x | 2011-01-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC | Credit Interpretation Request | 15 | Products used in Common uses (as defined by the credit) that do not contain PVC can be counted as compliant PVC product. The cost of these items can therefore be included in the overall cost of compliant PVC product. A material safety data sheet (MSDS) or a material data sheet that describe the composition of the products is the means to establish the product does not contain PVC. Costs of non PVC items must be accounted for as required for PVC.
x | x | x | x | x | x | x | x | 2012-08-01 | Mat-10 | Mat-7 | Mat-7 | Mat-6 | PVC | Technical Clarification | 16 | Where points for this credit are targeted, there is no requirement to submit documentation which demonstrates that PVC makes up more than 0.05% of the contract. Documentation proving the percentage of the contract spent is only required when the credit is claimed as ‘Not applicable’.
x | x | x | x | x | x | x | x |  | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber / Timber
x x x |  | x | x | x | x |  | x | 2010-01-01 |  | Mat-8 | Mat-8 | Mat-7 | Please note there is a revised version of this credit called 'Timber' which was released on 01/01/2010. If your project was registered after 01/01/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/materials-category/revised-timber-credit/2693.htm
| x | x | x | x | x | x | x | 2007-12-01 |  | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 1 | A current list of holders of the FSC chain-of-custody and management Certificate can be found on the following website: http://www.fsc-info.org/
x | x | [6 empty] | 2007-01-01 | Mat-11 | Mat-8 |  |  | Sustainable Timber | Technical Clarification | 2 | The last 'hands' to touch a FSC-certified piece of timber (e.g., reseller of a finished product) must have a Chain of Custody Certificate; otherwise there is no sure way to know that the timber product is in fact FSC-certified.
| x | x | x | x | x | x | x | 2007-12-01 |  | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to exclude formwork from items that must meet the Credit Criteria is denied. Green Star cannot assess whether formwork (or any other product) is reused in the future.
x | x | x | x | x | x | x | x | 2007-12-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 4 | It must be clear that the evidence accounts for all uses of the relevant material in the project, i.e. through using the word ‘all’ in the specification or, where appropriate, providing a summary table listing all uses and the attributes of the material(s) used.
| x | [6 empty] | 2007-12-01 |  | Mat-8 |  |  | Sustainable Timber | Technical Clarification | 5 | For a product to receive points within this credit for FSC certification, a full chain of custody (CoC) must exist. That is, if a board manufacturer who has FSC certification sells the board to a contractor for installation on the building, full chain-of-custody exists. However, if the board manufacturer provides product to the workstation manufacturer who doesn’t have FSC certification, who then sells it to the project, then CoC is lost, and points will not be awarded for that workstation. The following is an extract from the Forest Stewardship Council website: www.fsc.org
x | x | x | x | x | x | x | x | 2009-07-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Withdrawn | 6 | This Clarification was originally posted on Dec-07. Please see clarification No.14 for more information Chain-of-custody certification provides a guarantee about the production of FSC-certified products. Chain-of-custody is the path taken by raw materials from the forest to the consumer, including all successive stages of processing, transformation, manufacturing and distribution. Companies or individuals that process, transform, or trade (take ownership of) FSC certified forest products must be CoC certified. See Mat-8 Table No.1 for more information. *The last person in the chain of ownership for materials being supplied to the construction project does NOT need to be CoC certified, but the company those materials are being received from does. The important issue here is ownership. For example, a spec contractor must be CoC certified as they will not be the final owner of the FSC materials.
x | x | x | x | x | x | x | x | 2008-01-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 7 | Products made completely of laminate which are not pressed onto a wood-product substrate, (e.g. High-Pressure Laminate and Compact Laminate) are not considered to be composite wood products and are therefore not subject to the sustainable timber credit in Green Star Rating Tools.
| x | [8 empty] | Mat-8 |  |  | Sustainable Timber | Withdrawn | 8 | Refer to Technical Clarification No. 7 Products made completely of laminate that are not pressed onto a wood-product substrate, (e.g. High-Pressure Laminate and Compact Laminate) are not considered to be composite timber products for the purposes of Green Star and are therefore not subject to the Credit Criteria of this credit.
x | x | x | x | x | x | x | x | 2008-04-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 9 | For the purposes of this Credit, as there are no clear forestry standards that apply to bamboo, products manufactured from this material are not considered ‘timber’ and do not have to meet the Credit Criteria.
x | x | x | x | x | x | x | x | 2008-12-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | CIR Ruling | 10 | The Credit Interpretation Request to deem formwork that has certification other than that which is specified in the Technical Manual equivalent to meeting the Credit Criteria is denied. The revision of the timber credit is an ongoing project. Currently no major decisions have been made with regards to which direction this review will take.
x | x | x | x | x | x | x | x | 2009-02-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Correction | 11 | The following applies to all registered projects. The credit criteria for this credit has been modified from: "Two points are awarded where it is demonstrated that all timber and composite timber products used in the building and construction works are required to be sourced from either or a combination of the following:" It now reads: "Two points are awarded where it is demonstrated that 95% (by cost) of all timber and composite timber products used in the building and construction works are required to be sourced from either or a combination of the following:" All other credit criteria and compliance requirements remain as per the credit within the Technical Manual.
x | x | x | x | x | x | x | x | 2009-02-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 12 | For Green Star - As Built projects, where the cost of timber used in the project cannot be demonstrated via documentation from the supplier/sub-contractor, the project must submit a Quantity Surveyors’ report showing: - The total actual material cost of timber (existing timber if part of refurbishment) as a proportion of the project’s total value; and - For refurbishment projects claiming this credit, the volume and market value of timber material retained within the existing building.
| x | x | x | x | x | x | x | 2009-05-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 13 | The following applies to 95% of all formwork in a project for purposes of this credit: - New formwork must have Forest Stewardship Council certification. - Formwork that was new for this project that did not have Forest Stewardship Council certification, and was reused within this project cannot claim this credit. - Formwork that has been previously used in another project and has been used in this registered project can be deemed reused.
x | x | x | x | x | x | x | x | 2009-07-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 14 | The guidance on Chain of Custody for this credit has been updated. For timber products to receive points within the Green Star ’Sustainable Timber’ credit for the use of FSC certified timber, a full Chain of Custody (CoC) must exist through the supply chain to the project. That is, all FSC certified wood materials sourced by, and used on, the project must come from suppliers that have a valid FSC Chain of Custody certificate. For example, if a board manufacturer who has FSC certification sells the board to a contractor for installation on the building, full chain-of-custody exists to the project. However, if the board manufacturer provides product to the workstation manufacturer who doesn't have FSC certification, who then sells it to the project, then CoC is lost, and Green Star points can not be claimed. Entities that have been contracted/subcontracted to purchase, transform and/or install FSC certified wood specifically for the project do not need to be Chain on Custody holders themselves. Instead, these entities must prove (e.g. by providing invoices that include a current CoC code) that they have purchased the certified material directly from suppliers that have a valid Chain of Custody certificate. Click here to read the full document. http://www.gbca.org.au/green-star/materials-category/chain-of-custody-coc-guidance/2402.htm
x | x | x | x | x | x | x | x | 2010-01-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Timber | Correction | 15 | The Green Building Council of Australia announced in late November 2009, the release of a revised Timber credit effective January 1, 2010. This follows a detailed review of the GBCA's Timber credit, conducted by an independent Timber Expert Reference Panel. Projects that register after January 1, 2010 must use the revised version of the credit. Projects registered prior to this date have the option of continuing with the credit found in the Technical Manual, or using this revised version. Where projects registered prior to this date choose to use the revised version, this must be indicated on the cover page of this credit in their submission. To download this credit, please follow the link below, or click on this cell: http://www.gbca.org.au/green-star/materials-category/revised-timber-credit/2693.htm Prior Technical Clarifications and CIR Rulings for Mat-11 'Timber' (Office Interiors), Mat-8 'Sustainable Timber' (Office tools), Mat-7 'Sustainable Timber' (all other tools), do not apply to the new revised credit.
| x | x | x | x | x | x | x | 2012-08-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | Technical Clarification | 16 | Reused Timber Reused timber is defined as timber that is pre-existing in a fitout or building, or timber and / or timber products (flooring, walls and cladding, ceiling finishes, joinery, etc.) procured from a second hand source. Second hand sources may include, but are not limited to, second hand retailers, removalists, auction houses, and demolition works from previous sites. In order to establish timber is reused, in your submission, provide a short report including: - timber source information describing where there used timber was sourced; and - copies of receipts or delivery invoices from removalists or second hand retailers. Where pre-existing timber is used, provide inventory of timber items pre-existing in the building or fitout and which are retained.
x | x | x | x | x | x | x | x | 2012-08-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber/Timber | Technical Clarification | 17 | A project achieving at least 95% certification under the FSC Chain of Custody Standard for Project Certification (FSC-STD-40-006 V 1-0) or the PEFC standard for Project Certification (PEFC ST 2002:2010), is deemed to satisfy the requirements of the Timber credit in Green Star rating tools. Projects choosing to demonstrate compliance using this approach must provide the following documentation: - The FSC or PEFC project certificate. No other documentation is required.
x | x | x | x | x | x | x | x | 2012-08-01 | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Timber | Technical Clarification | 18 | Where points for this credit are targeted, there is no requirement to submit documentation which demonstrates that Timber makes up more than 1% of the contract. Documentation proving the percentage of the contract spent is only required when the credit is claimed as ‘Not applicable’.
|  | x | x | x | x | [5 empty] | Mat-9 | Mat-8
|  | x | x | x | x |  | x | 2008-12-01 |  |  | Mat-9 | Mat-9 | Design for Disasembly | Technical Clarification | 1 | Façade is defined as the exterior face of a building. ‘Face’ refers to the surface of a wall, masonry unit, or sheet of material that is exposed to view or designed to be exposed in finish work. The face will be the element in the façade that covers the surface layer of one material with another. Projects will need to consider the total surface area of the façade (as defined above) when calculating the designed for disassembly components.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 2 | Refurbishment Projects When the project is a refurbishment, the existing elements of the structure or the façade do not need to be included in the calculations for this Credit.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 3 | A disassembled component is defined as a structural or aesthetic element used in the construction of the project, independent from its fixings, so long as the fixings are sourced separately and the element is not manufactured with an attached fixing system. The fixings used in the construction of the structure may be designed for disassembly, but they do not need to form part of the calculation for this Credit. Fixings that have been extracted in the demolition process are usually made redundant as they become warped, bent and otherwise damaged and hence have no prospects for future use.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 4 | Where 'sacrificial formwork' to suspended concrete slab systems has been implemented (e.g. Bondek© style permanent aluminium formers), the formwork cannot be omitted from the calculation of the area of the structure being designed for disassembly. The formwork should be considered a part of the structure as it is in fact an extension of the concrete structure. The permanent formwork will most likely never be feasibly reused in the future.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 5 | A building that has been designed for quick demolition, with all materials to be sorted and transferred for recycling, does not meet the intent of the Credit. The aim of the credit is to design a building to be constructed of materials that can be removed for reuse elsewhere or in the reconstruction of the building. Demolishing the entire structure and recycling all materials, while still achieving some level of positive environmental impact, would diminish its practicality and undermine the positives gained from recycling as the embodied energy and resources used to achieve this would be extensive.
|  | x | x | x | x |  | x | 2011-01-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 6 | The surface area of structural elements exposed as part of the facade should not be counted when calculating the total area of the facade.
|  | x |  | x | x |  | x | 2012-08-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Technical Clarification | 7 | The requirement that 50% (by area) that structural framing, roofing and facade cladding systems must be designed for disassembly refers to a percentage of the total area of all these components, not 50% for each system.
|  | x | x | x | x |  | x | 2012-08-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | CIR Ruling | 8 | This ruling relates to the labelling requirements of this credit. Instead of labelling each element with all the required information (as listed in the Technical Manual), it is acceptable to provide a small label on each element which refers to the O&M Manual or Disassembly Plan. The O&M Manual or Disassembly plan must then contain all the required information for each element. If this approach is adopted then the following documentation is required (this is in addition the documentation listed in the Technical Manual). For Design ratings please provide: - Specification extract(s) where it is stated that the O&M Manual or Disassembly Plan must describe the labelling requirements in accordance with the Compliance Requirements and that a label will be attached to the relevant elements referring to this manual. For As-Built ratings please provide: - O&M Manual or Disassembly Plan extracts where the labelling information is provided (please also provide cover / contents pages); All other credit criteria are still applicable.
|  | x | x | x | x | x | x | 2013-11-01 |  |  | Mat-9 | Mat-9 | Design for Disassembly | Technical Clarification | 9 | The Credit Criteria for 95% of the total façade to be designed for disassembly only applies to new components of a building. For refurbishments, the percentage must be calculated from new elements only (including new elements attached to existing façade); for the purpose of this credit, previously existing elements may be excluded from the total area.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: * Quantity Surveyor report. * Comprehensive Disassembly Plan. * Confirmation of commitment of issue of Disassembly plan to the owner. Where the credit is claimed as 'Not Applicable' * Extract(s) from contract. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x |  |  | 2009-03-01 |  |  | Mat-9 | Mat-8 | Design for Disassembly | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Quantity Surveyor report. * Confirmation from the contractor. * Comprehensive Disassembly Plan * Confirmation of issue of the Disassembly Plan to the owner. Where the credit is claimed as 'Not Applicable' * Extract(s) from contract. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x |  | x | x |  |  |  | Mat-10 | Mat-9 | Dematerialisation
[8 empty] | 2008-11-01 |  |  |  | Mat-8 | Dematerialisation | Technical Clarification | M1 | In order to claim the size requirements criteria of this credit, the maximum unit size for each unit must be: - Studio apartment 35m2 - 1 bedroom apartment 50m2 - 2 bedroom apartment 70m2 - 3 bedroom apartment 95m2
|  | x | x | x | x | x | x | 2008-12-01 |  |  | Mat-9 | Mat-9 | Dematerialisation | withdrawn | 1 | Withdrawn 01-Nov-13. The Credit Criteria for 95% of the total façade to be designed for disassembly only applies to new components of a building. For refurbishments, the percentage must be calculated from new elements only (including new elements attached to existing façade); for the purpose of this credit, previously existing elements may be excluded from the total area.
|  | x | x | x |  |  |  | 2009-03-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Technical Clarification | 2 | The Credit Criteria for Piping in this credit, which states that 'No piping is used for urinals (i.e. all urinals are waterfree)', refers to water supply piping only.
|  | x | x | x |  |  | x | 2009-03-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Technical Clarification | 3 | The Credit Criteria for Piping in this credit, which states that 'No piping is used for toilets (i.e. all toilets are waterfree)', refers to water supply piping only.
|  |  |  | x |  |  |  | 2011-01-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Correction | 4 | Points are not awarded for 'Building Efficiency' in this credit for Green Star - Education v1. Design and As-Built Rating documentation requirements showing: 'Where Building Efficiency is achieved', can be disregarded for this credit.
[7 empty] | x | 2012-08-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Technical Clarification | 5 | External areas, defined as those areas that are outside the building envelope or incapable of being protected from the elements, are not considered for the calculation of unit size.
[7 empty] | x | 2013-11-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Technical Clarification | 6 | Where this credit refers to a ‘prefabricated module’ in relation to kitchens and bathrooms this must be interpreted as a kitchen or bathroom module, which is entirely ready-made offsite and positioned in the apartment and then connected to services. It does not mean a ‘modular’ kitchen or bathroom which is brought into the apartment in pieces and assembled onsite.
|  | x | x | x |  | x | x | 2009-03-01 |  |  | Mat-10 | Mat-9 | Dematerialisation | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where piping is minimised: * Short report. * Tender schematic hydraulic drawings. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  | x |  | Mat-2 |  |  | Mat-11 | Flooring
x |  |  |  | x | x |  | x | 2007-01-01 | Mat-2 |  |  | Mat-11 | Flooring | Technical Clarification | 1 | Whenever underlay is used, it must be assessed by the Flooring Calculator. The floor finish and underlay can be jointly entered into one line of the Calculator, in which case inputs should reflect "the weakest link" (e.g., durability should be assessed against the least durable of the two components). Otherwise, the floor finish and underlay can be entered into the Calculator separately (on separate lines). This will increase the "Total Floor Area within the Fitout", as the same floor area is deemed to be covered twice. The Certified Assessors will not award points unless the impact of the underlay has been taken into account.
x |  |  |  | x | x |  | x | 2008-03-01 | Mat-2 |  |  | Mat-11 | Flooring | Technical Clarification | 2 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
x |  |  |  | x | x |  | x | 2008-07-01 | Mat-2 |  |  | Mat-11 | Flooring | Technical Clarification | 3 | Hand-crafted rugs are considered a non-carpet floor covering material for the purposes of Green Star assessment, on the condition that they are non-fixed installations (e.g. not a wall to wall floor covering with underlay), that they are laid over an existing floor covering/finish, and that they are easily moved or removed.
x |  |  |  | x | x |  | x | 2010-03-01 | Mat-2 |  |  | Mat-11 | Flooring | Technical Clarification | 4 | Additional schemes have been recognised as environmentally innovative in this credit. Please see: http://www.gbca.org.au/green-star/materials-category/product-and-forest-certification-schemes/1616.htm
|  |  |  | x | x |  | x | 2012-08-01 | Mat-2 |  |  | Mat-11 | Flooring | Technical Clarification | 5 | It is acceptable to provide only performance requirements [i.e. no nomination of products] in the tender documentation for loose furniture, flooring, walls, partitions, joinery and ceiling products in place of the credit requirements for specification documentation, and include the requirement for the contractor to source these products. The tender documentation must state the specific performance requirement of products to the full extent that they are described in the Materials Calculator Guide [current at the time of project registration]. Where a GBCA-recognised Certification Standard is described, that Standard must be specifically named and the required level of that scheme's certification must be stated - simple reference to the GBCA web site is not sufficient. A combination of performance requirements and product nomination is also acceptable, i.e. some products may be nominated and others may be specified purely by performance requirements. Whenever a product is nominated it must be supported by all relevant manufacturer documentation. A copy of the relevant material calculator must be included in the submission. It must be completed based on the tender requirements. The number of points awarded are determined by the calculator.
[8 empty] | 2008-10-01 |  |  |  | Mat-9 | Floor Coverings | Technical Clarification | M1 | In order for this credit to be awarded, the following documentation must be provided - Copy of the Flooring Calculator completed for the project and referencing supporting documentation (below). - Short report prepared by a suitable professional that describes how Credit Criteria have been met by: - Summarising how the nominated flooring items meet the credit criteria; - Listing and referencing all the nominated flooring items in the project; and - Nominating which assessment categories (Environmentally Innovative, Reused, Eco Preferred Content, Modularity and Design for Disassembly) is achieved by each nominated flooring item. This must clearly correlate with the specification. - Extract(s) from the specification(s): - Outlining the assessment categories that each nominated flooring item must meet; - Requiring that the nominated flooring item meet the claimed assessment categories; - Requiring the contractor to obtain the approval of the design team or client before substituting the flooring listed in the specification; and - Indicating that any substituted items must meet the claimed assessment categories. - Flooring schedule nominating the quantities and type of flooring used in the project.
|  |  |  | x | x |  | x | 2009-03-01 | Mat-2 |  |  | Mat-11 | Flooring | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  |  |  | Mat-7 |  |  | Mat-12 | Joinery
x |  |  |  | x | x |  |  | 2007-08-01 | Mat-7 |  |  | Mat-12 | Joinery | Technical Clarification | 1 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
x |  |  |  | x | x |  |  | 2008-12-01 | Mat-7 |  |  | Mat-12 | Joinery | Technical Clarification | 2 | The final product’s (i.e. workstation, walls and partitions) onsite installer (i.e. carpenter or joiner etc) is not considered the manufacturer for the purpose of the Material Calculators. All the product elements from one or more supplier should be entered into one line of the Calculator, and inputs should reflect 'the weakest link', should there be a difference (e.g. durability should be assessed against the least durable of the components).
x | [7 empty] | 2009-05-01 | Mat-7 |  |  | Mat-12 | Joinery | Technical Clarification | 3 | For workstation storage units refer to Mat-1/6 (Office Interiors) or Mat-13/6 (all other tools).
|  |  |  | x | x |  | x | 2012-08-01 | Mat-7 |  |  | Mat-12 | Joinery | Technical Clarification | 4 | It is acceptable to provide only performance requirements [i.e. no nomination of products] in the tender documentation for loose furniture, flooring, walls, partitions, joinery and ceiling products in place of the credit requirements for specification documentation, and include the requirement for the contractor to source these products. The tender documentation must state the specific performance requirement of products to the full extent that they are described in the Materials Calculator Guide [current at the time of project registration]. Where a GBCA-recognised Certification Standard is described, that Standard must be specifically named and the required level of that scheme's certification must be stated - simple reference to the GBCA web site is not sufficient. A combination of performance requirements and product nomination is also acceptable, i.e. some products may be nominated and others may be specified purely by performance requirements. Whenever a product is nominated it must be supported by all relevant manufacturer documentation. A copy of the relevant material calculator must be included in the submission. It must be completed based on the tender requirements. The number of points awarded are determined by the calculator.
|  |  |  | x | x |  |  | 2009-03-01 | Mat-7 |  |  | Mat-12 | Joinery | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the supplier All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  |  |  | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture
x |  |  |  | x | x |  |  | 2006-01-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 1 | A product that has been awarded the Good Environmental Choice label by the Australian Environmental Labeling Association (AELA) automatically achieves 'product score' of 100 in the calculators. Choose 'Environmentally Innovative' under the pull-down menu for Product Type. These products need to present no documentation for the assessment besides their AELA Certificate.
x |  |  |  | x | x |  |  | 2006-01-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 2 | Reused components (e.g., tabletop) count towards the 'Eco-preferred Content' of a product, assuming relevant evidence is available.
x |  |  |  | x | x |  |  | 2006-09-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 3 | For 'Durability', evidence for "<7 years" does not need to be provided as it does not increase the 'Product Score'.
x |  |  |  | x | x |  |  | 2006-09-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 4 | All columns of the Calculators refer to the entire product. 'Durability 'may be established against only the 'white' (non-upholstered) item IF the 'white' item is clearly designed for disassembly to allow for reupholster AND the supplier of the upholstering fabric commits to product stewardship (reclaiming the current fabric if the tenant chooses to reupholster). In all other cases, 'Durability' must be documented against the 'weakest link' of the product. For example, if the fabric has warranty for 10 years and the 'white' chair - for over 15 years, enter '7 to 10 years' in the cell.
x |  |  |  | x | x |  |  | 2006-09-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 5 | Where evidence is provided for ISO 14001 certification of the EMS, evidence of EMS is not necessary.
x | [7 empty] | 2009-05-01 | Mat-1 |  |  | Mat-13 | Workstations | withdrawn | 6 | This clarification has been withdrawn, please refer to technical clarification no.9 (below) A workstation consist of the work surface itself, the storage element(s) and screening device(s). elements, they are considered a 'workstation' for the purpose of Mat-1 'Workstations'. The complete should be entered into one line of the Calculator, and inputs should reflect 'the weakest link' should there be a difference (e.g., durability should be assessed against the least durable of the components). within the respective Mat-3 'Walls & Partitions' and Mat-6 'Storage' Calculators.
x |  |  |  | x | x |  |  | 2007-01-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 6 | A workstation consists of the work surface itself, the storage element(s) and screening device(s). All those elements from one manufacturer can be considered a 'workstation' for the purpose of Mat-1 'Workstations'. The complete workstation should be entered into one line of the Calculator, and inputs should reflect 'the weakest link' should there be a difference (e.g., durability should be assessed against the least durable of the components). All individually purchased storage units and partitions shall be assessed within the respective Mat-3 'Walls & Partitions' and Mat-6 'Storage' Calculators.
x |  |  |  | x | x |  |  | 2007-01-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 7 | Product stewardship is a product-centred approach to environmental protection that implies that those in the product's life cycle (e.g., manufacturers, retailers, users) need to share responsibility for reducing its environmental impact. Practically, product stewardship is understood as the supplier's service to the customer to collect the product for reuse, recycling or reprocessing whenever the customer no longer requires its service.
x |  |  |  | x | x |  |  | 2006-01-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 8 | With regards to product stewardship, as an interim step in the industry's transition, Green Star - Office Interiors v1 and Green Star - Office Interiors v1.1 allow for this commitment to take force "at the end of [the product's] service life", e.g. after the warranty period has expired. The submission must include the supplier's contractual obligation to collect the product for reuse, recycling or reprocessing. The Certified Assessor(s) look for a confirmation that the item will not be sent to the landfill, such as a description of what will happen to the product and what facilities or arrangement will enable the supplier to divert it from landfill.
x |  |  |  | x | x |  |  | 2009-05-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Correction | 9 | This clarification applies to all projects registered after this date. Projects registered prior to this date may choose to follow this correction, but are not required to. A workstation may consist of the work surface itself, the storage element(s) and screening device(s). When all these elements are mechanically integrated, they are considered a 'workstation' for the purpose of Mat-1 'Workstations'. The complete assembly should be entered into one line of the Calculator, and inputs should reflect 'the weakest link' should there be a difference (e.g., durability should be assessed against the least durable of the components). In the event that the storage element(s) and screening device(s) are detached from the work surface, they shall be considered ‘Partitions’ and ‘Storage Units’ within the respective Mat-3 'Walls & Partitions' and Mat-6 'Storage' Calculators.
|  |  |  | x |  |  |  | 2012-08-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Technical Clarification | 10 | Lecture, theatre or other types of joined seating, should be considered as Loose Furniture for the purpose of the credit. The number of chairs should be documented on the basis of the number of individual seats.
|  |  |  | x | x |  |  | 2012-08-01 |  |  |  | Mat-13 | Loose Furniture | Technical Clarification | 11 | It is acceptable to provide only performance requirements [i.e. no nomination of products] in the tender documentation for loose furniture, flooring, walls, partitions, joinery and ceiling products in place of the credit requirements for specification documentation, and include the requirement for the contractor to source these products. The tender documentation must state the specific performance requirement of products to the full extent that they are described in the Materials Calculator Guide [current at the time of project registration]. Where a GBCA-recognised Certification Standard is described, that Standard must be specifically named and the required level of that scheme's certification must be stated - simple reference to the GBCA web site is not sufficient. A combination of performance requirements and product nomination is also acceptable, i.e. some products may be nominated and others may be specified purely by performance requirements. Whenever a product is nominated it must be supported by all relevant manufacturer documentation. A copy of the relevant material calculator must be included in the submission. It must be completed based on the tender requirements. The number of points awarded are determined by the calculator.
|  |  |  | x | x |  |  | 2009-03-01 | Mat-1 |  |  | Mat-13 | Workstations / Loose Furniture | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  |  |  | Mat-4 |  |  | Mat-13 | Chairs / Loose Furniture
x |  |  |  | x | x |  |  | 2007-08-01 | Mat-4 |  |  | Mat-13 | Chairs / Loose Furniture | Technical Clarification | 1 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
x |  |  |  | x | x |  |  | 2011-01-01 | Mat-4 |  |  | Mat-13 | Chairs | Technical Clarification | 2 | Lounges are to be included in this credit. Lounges are defined as a seat for one or more person used for informal seating or reclining. Some examples of lounges include sofas and chaise lounges.
|  |  |  | x | x |  |  | 2009-03-01 | Mat-4 |  |  | Mat-13 | Chairs / Loose Furniture | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  |  |  | Mat-5 |  |  | Mat-13 | Tables / Loose Furniture
x |  |  |  | x | x |  |  | 2007-08-01 | Mat-5 |  |  | Mat-13 | Tables / Loose Furniture | Technical Clarification | 1 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
|  |  |  | x | x |  |  | 2009-03-01 | Mat-5 |  |  | Mat-13 | Tables / Loose Furniture | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  | x | x |  |  |  | Mat-6 |  |  | Mat-13 | Storage / Loose Furniture
x |  |  |  | x | x |  |  | 2007-08-01 | Mat-6 |  |  | Mat-13 | Storage / Loose Furniture | Technical Clarification | 1 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
x | [7 empty] | 2009-10-01 | Mat-6 |  |  | Mat-13 | Storage / Loose Furniture | Technical Clarification | 2 | For the purposes of this credit, storage products are defined in two ways: 1) non-joinery items which are made from materials other than wood (e.g. steel or plastic) and custom-built/installed on site or prefabricated off site and installed on site for intended use as storage; and 2) items which are available as off-the-shelf prefabricated products (including wood) which are intended to be used for storage purposes. Examples include, but are not limited to, filing cabinets, compactus units, tambour cabinets, and shelving units.
|  |  |  | x | x |  |  | 2009-03-01 | Mat-6 |  |  | Mat-13 | Storage / Loose Furniture | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  |  | x |  |  |  | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions
x |  |  |  |  | x |  |  | 2007-01-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 1 | Doors are excluded from this Calculator.
x | [7 empty] | 2007-01-01 | Mat-3 |  |  |  | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 2 | All tenant-installed partitions (including the stud-and-gypsum partitions constructed on site) are to be included in the 'Walls & Partitions' Calculator.
x |  |  |  |  | x |  |  | 2009-05-01 | Mat-3 |  |  | Mat-13 | Walls and Partitions | withdrawn | 3 | See clarification Mat-1/9 (Green Star - Office Interiors) or Mat-13/9 (Green Star - Healthcare v1, Green Star - Education v1) for more information Workstation partitions are considered partitions, not workstations.
x |  |  |  |  | x |  |  | 2007-08-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 4 | As stipulated within the Technical Manual, the "Built Zone" must be enclosed by full height walls or partitions therefore it only includes areas enclosed on all four sides. However, any space that is enclosed by full height walls and/or partitions on four sides is a 'built zone', regardless of whether the enclosure is solid or interrupted by glazing or openings (e.g. full height door opening with no door).
x | [7 empty] | 2008-03-01 | Mat-3 |  |  |  | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 5 | Any base building walls are excluded from the Mat-3 ‘Walls and Partitions Calculator’. Only non-bearing tenant partitions are to be included.
x |  |  |  |  | x |  |  | 2008-03-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | CIR Ruling | 6 | The Credit Interpretation Request (CIR) to exclude the retained walls in a refurbishment from the area of the built zones calculation is granted conditionally on the project’s ability to demonstrate that the walls were existing, by providing either: - Construction plan drawings with the relevant existing partitions clearly indicated and a letter from the tenancy architect confirming the walls existed prior to any tenancy work and are at least 1 year old; OR - Drawings of the previous tenancy, indicating the existing walls that are being retained. The date on the drawing must be highlighted to confirm the walls are at least 1 year old. In addition, if the retained walls are to be excluded from the built zone calculation, they must also be excluded from the Mat-3 ‘Walls and Partitions Calculator’ (i.e. cannot be claimed as ‘reused’).
x |  |  |  |  | x |  |  | 2008-03-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 7 | Acceptable documentation for Good Environmental Choice Australia (GECA) certified products 1. A copy of the GECA License Agreement for the nominated product(s); OR 2. Printout(s), dated within 12 months immediately preceding the Round 1 submission, from the Products Register of the GECA website.
x | [7 empty] | 2008-06-01 | Mat-3 |  |  |  | Walls and Partitions / Ceilings, Walls and Partitions | Technical Clarification | 8 | If toilet and shower partitions are provided (installed and paid for) by the base building as a previous or separate exercise to the tenancy fitout, then these materials are not required to be documented in the Walls and Partitions Calculator in the Green Star - Office Interiors rating tool.
x |  |  |  |  | x |  |  | 2008-12-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions | Technical Clarification | 9 | Where 90% or more (by mass) of the components of a wall/partition can be categorised as ‘Environmentally Innovative’, the project may enter the entire wall/partition as ‘Environmentally Innovative’ in the calculator and may disregard any non-compliant components.
x | [7 empty] | 2008-12-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions | Technical Clarification | 10 | For the purposes of this credit, meeting pods, which may or may not be structurally part of the base building, are considered built zones. They are ultimately enclosures that will be fitted out with wall/ceiling finishes & doors.
x | [6 empty] | x | 2009-10-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Withdrawn | 11 | Originally posted Dec-08. See TC. Mat-0/12 for more information. The final product’s (i.e. workstation, walls and partitions) onsite installer (i.e. carpenter or joiner etc) is not considered the manufacturer for the purpose of the Material Calculators. All the product elements from one or more supplier should be entered into one line of the Calculator, and inputs should reflect 'the weakest link', should there be a difference (e.g., durability should be assessed against the least durable of the components).
x |  |  |  |  | x |  |  | 2009-07-01 | Mat-3 |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Proposed Technical Clarification | 12 | For the purposes of this credit, any solid, non-load bearing area divider installed as part of the fitout works should be included within the calculator and accounted for within the Green Star submission, provided that it has not yet been accounted for in the 'Workstations / loose furniture' credit.
[5 empty] | x |  | x | 2012-08-01 |  |  |  | Mat-14 | Ceilings, Walls and Partitions / Internal Walls | Technical Clarification | 13 | It is acceptable to provide only performance requirements [i.e. no nomination of products] in the tender documentation for loose furniture, flooring, walls, partitions, joinery and ceiling products in place of the credit requirements for specification documentation, and include the requirement for the contractor to source these products. The tender documentation must state the specific performance requirement of products to the full extent that they are described in the Materials Calculator Guide [current at the time of project registration]. Where a GBCA-recognised Certification Standard is described, that Standard must be specifically named and the required level of that scheme's certification must be stated - simple reference to the GBCA web site is not sufficient. A combination of performance requirements and product nomination is also acceptable, i.e. some products may be nominated and others may be specified purely by performance requirements. Whenever a product is nominated it must be supported by all relevant manufacturer documentation. A copy of the relevant material calculator must be included in the submission. It must be completed based on the tender requirements. The number of points awarded are determined by the calculator.
[5 empty] | x |  |  | 2009-03-01 |  |  |  | Mat-14 | Walls and Partitions / Ceilings, Walls and Partitions | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x | 2013-11-01 |  |  |  | Mat-14 | Internal Walls | Documentation (As Built) | B | Based on feedback from assessors and project teams, the following documentation is no longer required at the time of a Green Star – As Built submission for this credit. *Access Review Report *Short Report dot point 3: ‘Demonstrating that all publicly accessible areas and at least 10% of dwellings have been designed to comply with class A, B or C requirements of AS4299-1995. Projects must submit the following documentation instead: *Copy of the Internal Walls Calculator completed for the project and referencing supporting documentation *Short Report presented by a suitable professional that describes how Credit Criteria have been met by: o Summarising how the nominated internal walls meet the credit criteria o Listing and referencing all the nominated internal walls in the project; and o Nominating which assessment categories in the calculator have been achieved by the internal walls. This must clearly correlate with the ‘confirmation from the supplier(s)’ and the ‘manufacturer documentation’. All other documentation must be provided as per the Technical Manual at the time of submission.
x |  |  |  |  | x |  |  |  | Mat-8 |  |  | Mat-14 | Ceilings / Ceilings, Walls and Partitions
x | [7 empty] | 2008-12-01 | Mat-8 |  |  | Mat-14 | Ceilings / Ceilings, Walls and Partitions | Technical Clarification | 1 | An integrated fitout project within a new building can claim this credit, provided that the ceilings have been built in accordance with the tenant’s specifications. The project will need to provide documentation as per the Compliance Requirements of the Technical Manual for ‘Ceiling Tiles Left Intact’.
[5 empty] | x |  |  | 2009-03-01 | Mat-8 |  |  | Mat-14 | Ceilings / Ceilings, Walls and Partitions | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x |  |  |  |  | Mat-15 | Universal Design
[7 empty] | x | 2013-11-01 |  |  |  | Mat-15 | Universal Design | CIR Ruling | 1 | Projects that provide at least 10% of dwellings that meet the Platinum Level of the Livable Housing Design Guidelines are deemed to meet the requirements for one point in this credit. Please refer to Documentation (Design) A and Documentation (As Built) B for documentation requirements which must be adhered to when adopting this approach.
[7 empty] | x | 2013-11-01 |  |  |  | Mat-15 | Universal Design | Documentation (Design) | A | To be used in conjuction with Mat-15 CIR Ruling 1 only. Submit all the evidence and ensure it readily confirms compliance. • Provisional Livable Housing Design Certificates -OR- • Short report • Tender drawing(s) • Extract(s) from the specifications Copies of the Platinum Level Provisional Livable Housing Design Certificates (issued for the design of dwellings) for at least 10% of dwellings issued by Livable Housing Australia. Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: • Referencing supporting documentation and describing, with calculations and summary tables wherever appropriate, how the Credit Criteria have been achieved; and • Demonstrating that at least 10% of dwellings have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. Tender drawing(s) marked up to show the features which have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. Extract(s) from the specifications demonstrating how the dwellings comply with the Platinum Level requirements of the Livable Housing Design Guidelines.
[7 empty] | x | 2013-11-01 |  |  |  | Mat-15 | Universal Design | Documentation (As Built) | B | To be used in conjuction with Mat-15 CIR Ruling 1 only. Submit all the evidence and ensure it readily confirms compliance. • Final Livable Housing Design Certificates -OR- • Short report • As-built drawing(s) Copies of the Platinum Level Final Livable Housing Design Certificates (issued for the constructed dwellings) for at least 10% of dwellings issued by Livable Housing Australia. Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: • Referencing supporting documentation and describing, with calculations and summary tables wherever appropriate, how the Credit Criteria have been achieved; and • Demonstrating that at least 10% of dwellings have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. As-built drawing(s) marked up to show the features that have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines.
x | [8 empty] | Mat-9 |  |  |  | Waste Management for Tenancy Operation
x | [7 empty] | 2006-01-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | Technical Clarification | 1 | Storage space provisions of this credit are in addition to base building provisions and must provided on each floor of a multi-storey tenancy.
x | [7 empty] | 2007-12-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | Withdrawn | 2 | The following clarification is being modified. Please see Technical Clarificaiton No. 6 for more information It is acceptable to meet the Credit Criteria of Mat-9 'Waste Management for Tenancy Operation' with more than one dedicated storage area. However, all storage areas dedicated to recycling must meet all the Credit Criteria and Additional Guidance requirements and be functional (e.g., an area may not be so small that it cannot house at least 3 bins). An area dedicated exclusively to storage of rubbish (non-recycling waste) should be excluded. In addition, where other tenants are present in the building, it must be clearly demonstrated that the fitout's use of the recycling waste storage facilities is not compromised (e.g., how a proportion of facilities is dedicated for exclusive use of the fitout).
x | [7 empty] | 2008-03-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to have a smaller designated recycling space combined with the use of a compaction device be deemed equivalent to providing a sufficiently sized recycling storage space is denied. Although installed as a permanent feature, the use of a compactor device is considered operational.
x | [7 empty] | 2008-04-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | CIR Ruling | 4 | The Credit Interpretation Request (CIR) to deem at-desk storage for recycling of typical office waste an equivalent means of meeting Credit Criteria is granted conditionally on the project’s ability to clearly demonstrate that: - The size of the centralised dedicated recycling storage space is at least 30% of the total required designated recycling storage area as stated in the Credit Criteria; - The remainder of the dedicated recycling storage space is distributed throughout the fitout in the form of recycling-only at-desk storage;
x | [7 empty] | 2008-04-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | CIR Ruling | 4 | - The waste is removed from the at-desk storage bins at least three times a week and stored in an area within the base building that is accessible to the waste contractor. Acceptable evidence includes an extract from the lease conditions or confirmation from the base building owner; - The waste recycling service provider is required to liaise with the tenancy or base building’s cleaning contractor to ensure that information and training on multiple waste stream source separation process is provided to cleaning staff. An excerpt from the contract stating this requirement must be provided as evidence
x | [7 empty] | 2009-02-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to deem a waste management and recycling system with 1m2 of designated recycling storage space per 12 workstations with fortnightly collections an equivalent means of meeting the Mat-9 ‘Waste Management for Tenancy Operation’ Credit Criteria is granted. Projects are required to address the Compliance Requirements and include all documentation within the submission.
x | [7 empty] | 2007-12-01 | Mat-9 |  |  |  | Waste Management for Tenancy Operation | Technical Clarification | 6 | It is acceptable to meet the Credit Criteria of Mat-9 'Waste Management for Tenancy Operation' with more than one dedicated storage area. However, all storage areas dedicated to recycling must meet all the Credit Criteria and Additional Guidance requirements and be functional (e.g., an area may not be so small that it cannot house at least 3 bins). An area dedicated exclusively to storage of rubbish (non-recycling waste) should be excluded. In addition, where other tenants are present in the building, it must be clearly demonstrated that the fitout's use of the recycling waste storage facilities is not compromised (e.g., how a proportion of facilities is dedicated for exclusive use of the fitout). Please note: The reference to 3 bins is meant as a guide only and does not stipulate a definitive requirement. The objective of this example is to ensure that designated recycling storage areas provide ample space for ease of maneuvering and access to and from the bins. Each project must design their designated spaces accordingly.
Note on Q45: zkuypers: Elham - I'm pretty sure that we have been asked to approve different combinations of storage space and collection frequency - like weekly/fortnightly. Am I imagining this (possibly!) if that's the case then we should word htis ruling to allow for all possible combinations.

## Eco (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Land Use and Ecology
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
| x | x | x | x | x | x | x |  |  | Eco General | Eco General | Eco General | General
| x | [6 empty] | 2008-07-01 |  | Eco-0 |  |  | General | Technical Clarification | 1 | Definition: Wetland: Wetlands are areas that are wet for long enough periods that the plants and animals living in or near them are adapted to, and often dependent on, wet conditions for at least part of their life cycle. For the purpose of the policy, wetlands are defined as land that is: - Inundated with water on a temporary or permanent basis - Inundated with water that is usually slow moving or stationary - Inundated with water that is shallow - Inundated with water that may be fresh, brackish or saline. From NSW Wetlands Policy 1996, (http://www.naturalresources.nsw.gov.au/water/wetlands_facts.shtml )
| x | x | x | x | x | x | x | 2011-01-01 |  |  |  |  | Site Purchase | Technical Clarification |  | The credits for: Eco-Conditional Requirement, Topsoil, Re-use of Land and Change of Ecological Value are to be applied to the state of the site that existed at the date of site purchase. In cases where the site has been owned by the current owner for more than five years (from the project’s Green Star registration date), it is to be applied to the state of the site that existed at least five (but not more than ten years) prior to the project’s Green Star registration date. Note that the following documentation, required in the General section of the Green Star submission forms part of the Compliance Requirements for this Conditional Requirement: Where the site has been owned by the current owner for less than five years (from the project’s Green Star registration date): • Scaled site plans OR aerial photographs generated prior to site purchase (but not more than ten years prior to site purchase), marked up as necessary to be clearly showing: – Whether the site was a greenfield or brownfield site, and whether it contained any buildings; – The footprint area of any buildings that existed on the site; – The land types that were present on site in accordance with Eco-4 Change of Ecological Value Calculator; and – The areas that existed in a radius no less than 100 metres around the site. AND – Evidence of site purchase clearly indicating the site purchase date and any relevant site attributes. Where the site has been owned by the current owner for more than five years (from the project’s Green Star registration date): • Scaled site plans OR aerial photographs generated at least five years (but not more than ten years) prior to the project’s Green Star registration date, marked up as necessary to be clearly showing: – Whether the site was a greenfield or brownfield site, and whether it contained any buildings; – The footprint area of any buildings that existed on the site; – The land types that were present on site in accordance with Eco-4 Change of Ecological Value Calculator; and – The areas that existed in a radius no less than 100 metres around the site. AND – Evidence of the fact that the site has been owned by the current owner for more than five years (from the project’s Green Star registration date).
| x | x | x | x | x | x | x |  |  | Eco-1 | Eco | Eco | Conditional Requirement
| x x x | x | x | x | x | x | x | 2009-03-01 |  | Eco-1 | Eco | Eco | Please note there is a revised version of this credit which was released on 01/03/2009. If your project was registered after 01/03/2009, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/eco-conditional-requirement-eco-1-ecological-value-of-site/2085.htm
| x | x | x | x | x | x | x | 2008-01-01 |  | Eco-1 | Eco | Eco | Conditional Requirement / Ecological Value of Site | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to submit the following documentation instead of the local Development Control Plan and Development Zone Map stipulated in the Technical Manual is granted: 1. Relevant domain map; 2. Relevant ‘special facilities’ schedule from the Local Council Planning Scheme together with the approved Master Plan; and 3. Original Rezoning Agreement referred to in the Local Council Planning Scheme.
| x | x | x | x | x | x | x | 2009-03-01 |  | Eco-1 | Eco | Eco | Conditional Requirement | Correction | 2 | This credit has been revised as per the criteria set out in the following link: http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/eco-conditional-requirement-eco-1-ecological-value-of-site/2085.htm Projects registered prior to 18th of March 2009 can choose to use this new criteria or the previous version of this credit. Projects registered after the 18th of March can only use the new version of this credit.
| x | x | x | x | x | x | x |  |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal
| x | x | x | x | x | x | x | 2008-01-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to provide a letter from the Architect stating that the project has no cut and fill or removal of topsoil from the site as evidence for Eco-1 ‘Topsoil’ instead of the documentation required by the Technical Manual is denied as this would not equivalently demonstrate compliance.
| x | x | x | x | x | x | x | 2008-01-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | Technical Clarification | 2 | The ‘site’ is defined by the scope of Green Star assessment. If a development consists of several buildings, the site must be defined for each registered building. Stockpiling of soil on sites of the other buildings within the development is not acceptable.
| x | [6 empty] | 2008-10-01 |  | Eco-5 |  |  | Topsoil / Topsoil and Fill Removal | Correction | 3 | Applies to all projects registered from November 2008 It is not the intention of the credit to penalise the refurbishment of buildings. For this reason, and to ensure consistency between Green Star – Office Design v2 and Green Star – Office As Built v2, where the project is a refurbishment this credit is ‘Not Applicable’ and is excluded from the points available to calculate the Land Use & Ecology Category Score. Previously, no points would be awarded to refurbishments.
|  |  | x | x | x |  | x | 2011-01-01 |  |  |  |  | Topsoil / Topsoil and Fill Removal | Technical Clarification | 4 | The following documentation is required where the credit is claimed as 'Not Applicable': Short report • Where the credit is claimed as ‘Not Applicable’ because the topsoil on site is considered to be inherently non-productive, summarising the reasoning behind this determination, and citing evidence from the suitably qualified professional. Report by a suitably qualified professional • Stating that the topsoil on site has been found to be inherently non-productive; • Providing a description of the condition of the topsoil on site; and • Justifying the determination that the topsoil on site is inherently non-productive. Suitably qualified professional For the purposes of this credit a suitably qualified professional is a person such as a professional soil technician or agronomist.
|  | x | [5 empty] | 2012-08-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | Technical Clarification | 5 | The credit may be claimed as ‘Not Applicable’ and the points available excluded from calculation of the Land Use and Ecology Category Score where: - No topsoil on site was affected by the construction/refurbishment works; or - The topsoil on site is inherently non-productive. Topsoil that is inherently non-productive may be affected by one or more of the following problems: - Very poor capacity to store water - Excessive salinity, acidity, or alkalinity; - Very low nutrient availability; - Poor physical status of surface and subsoil horizons e.g. excessively hard, compact and/or impermeable. When claiming the credit as not applicable provide the following: - Report by a suitably qualified professional including: - statement that no topsoil on site was affected by the construction/refurbishment works; - summarising why this was the case; OR - statement that the topsoil on site has been found to be inherently non-productive; - a description of the condition of the topsoil on site; and - justification of the determination that the topsoil on site is inherently non-productive. A suitably qualified professional for the purpose of this credit is a person with experience in the study of soil and soil properties. Examples include soil technician, landscape architect or agronomist.
[8 empty] | 2008-10-01 |  |  |  | Eco-4 | Topsoil and Fill Removal from Site | Technical Clarification | M1 | As per Additional Guidance for this credit in the Green Star – Office v3 Technical Manual, the credit cannot be claimed where a portion of the topsoil is being removed from the site
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | Documentation (Design) | A | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | Documentation (As Built) | B | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
| x |  | x | x | x | x |  | 2013-11-01 |  | Eco-5 | Eco-1 | Eco-1 | Topsoil / Topsoil and Fill Removal | Documentation (As Built) | B | For As Built projects The following simplified documentation pathway is available for projects which were awarded this credit as being 'not applicable' to their project at the Design stage for either of the following reasons: 1. The project is refurbishment; or 2. The topsoil on site is inherently non-productive. Projects which wish to claim this credit as being 'not applicable' because no topsoil was impacted by the construction works must provide documentation as per the Technical Manual to be assessed at the As Built stage. This credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage (as outlined above). To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x |  |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land
| x | x | x | x | x | x | x | 2008-10-01 |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land | Technical Clarification | 1 | A carpark demonstrated to have existed at the time of site purchase (or at least two years prior to the commencement of the project) is considered to be ‘previously developed land’. Please note that to ensure that the Aim of the Credit is met, the Certified Assessors will look for evidence that the site had indeed been developed and that the car park is/was legitimate.
| x | x | x | x | x |  | x | 2009-03-01 |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land | Technical Clarification | 2 | ‘Previously developed land’ is land that is or was occupied by a permanent structure, including the curtilage of the developed land and any associated fixed surface infrastructure. The definition excludes: * Land that has been developed for minerals extraction or waste disposal by landfill purposes where provision for restoration has been made through development control procedures; and * Land that was previously developed but where the remains of the permanent structure or fixed surfaces have blended into the landscape in the process of time (to the extent that it can reasonably be considered as part of the natural surroundings). ‘Curtilage’ is defined as the enclosed area immediately surrounding a building or dwelling including yards and paved surfaces'
|  | x | x | x |  |  |  | 2011-01-01 |  | Eco-2 | Eco-2 | Eco-2 | Re-use of Land | Documentation (Design and As Built) | 3 | The credit criteria that reads "If at the time of site purchase, 75% of the site has been previously built on." May be replaced with: "75% of the site was Previously Developed Land" at the time of site purchase." Where this alternative credit criteria is used, a short report from the architect must be provided as follows: • Where 75% of the site was 'previously developed land': -Describe the site area that was 'previously developed land' at the time of purchase; -Specify what proportion of the site was 'previously developed land' at the time of purchase and justify all figures quoted; -Reference the documentation submitted in the 'General' section of the submission. • Where the project is a building extension: -Describe the site area that was 'previously developed land' at the time of purchase; -Reference the documentation submitted in the 'General' section of the submission, showing that the extension boundaries are wholly within an area of the site that was 'previously developed land'. • Where the project is a refurbishment: -State that this is so; -Reference the documentation submitted in the 'General' section of the submission.
[5 empty] | x |  | x | 2011-01-01 |  | Eco-2 | Eco-2 | Eco-2 | Re-use of Land | Documentation (Design and As Built) | 4 | The credit criteria that reads "If at the time of site purchase, buildings have occupied a minimum of 75% of the site." May be replaced with: "75% of the site was Previously Developed Land" at the time of site purchase." Where this alternative credit criterion is used, a short report from the project architect must be provided as follows: • Where 75% of the site was 'previously developed land': Describe the site area that was 'previously developed land' at the time of purchase; -Specify what proportion of the site was 'previously developed land' at the time of purchase and justify all figures quoted; -Reference the documentation submitted in the 'General' section of the submission. • Where the project is a building extension: -Describe the site area that was 'previously developed land' at the time of purchase; -Reference the documentation submitted in the 'General' section of the submission, showing that the extension boundaries are wholly within an area of the site that was 'previously developed land'. • Where the project is a refurbishment: -State that this is so; -Reference the documentation submitted in the 'General' section of the submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land | Documentation (Design) | A | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land | Documentation (As Built) | B | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
| x |  | x | x | x | x |  | 2013-11-01 |  | Eco-2 | Eco-2 | Eco-2 | Reuse of Land | Documentation (As Built) | C | For As Built projects Points for this credit are automatically awarded, following the successful award of points at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x |  |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land
| x | x | x | x | x | x | x | 2007-08-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem this credit ‘Not Applicable’ (na) for projects that are assessed as ‘Building Extensions’ is granted because it meets the Aim of Credit in an equivalent manner to that of refurbishment projects.
| x | x | x | x | x | x | x | 2007-08-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 2 | Please note the contamination resulting from this development (e.g. with asbestos from demolition of the existing buildings) cannot contribute to this credit.
| x | [6 empty] | 2007-08-01 |  | Eco-3 |  |  | Reclaimed Contaminated Land | Technical Clarification | 3 | The GBCA will not act to determine, from evidence of site visits, whether land is contaminated. This determination must be made by the relevant expert, as stipulated in the Technical Manual. The Certified Assessor(s) will accept that expert’s conclusion and seek to verify that the land is decontaminated in accordance with the Technical Manual.
| x | [6 empty] | 2007-08-01 |  | Eco-3 |  |  | Reclaimed Contaminated Land | Technical Clarification | 4 | The second bullet point, “certificate from the Environmental Auditor confirming that the site has been correctly and appropriately decontaminated", does not refer to a Certificate of Environmental Audit but to a confirmation from the Auditor. For the confirmation from the Environmental Auditor to be acceptable, the Auditor must meet the requirements of the National Environment Protection Measure, specifically Schedule B (10).
| x | x | x | x | x | x | x | 2007-08-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | CIR Ruling | 5 | The Credit Interpretation Request (CIR) to deem “a letter from a qualified (in the area of soil remediation) consultant who has been involved in the development, documenting pre-existing conditions and remediation procedures undertaken, and confirming that the site has been made suitable for development, safe for human health and the environment” sufficient for demonstrating that “adequate remedial steps have been taken to decontaminate the site prior to construction” (as per the Technical Manual) is granted.
| x | x | x | x | x | x | x | 2007-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 6 | The statement “prior to construction” as stated in the Eco-3 Credit Criteria refers to construction of actual building structures, not to the beginning of any construction works on the project (e.g. land clearing). Thereby, if remediation occurs during earthworks or any other stages during the construction phase of a project prior to the building of any structure, it is still considered as “prior to construction”.
| x | x | x | x | x | x | x | 2007-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | CIR Ruling | 7 | Green Star - Design: The Credit Interpretation Request (CIR) to deem a commitment to remediate a contaminated site at a later date equivalent to full remediation of the site prior to Green Star – Design submission is granted conditionally on the project’s ability to demonstrate all of the following in the submission: - No construction works have commenced on the site at the date of the Round 2 assessment; - There is assurance that the site will be remediated as stipulated, i.e. the builder has been appointed and has a contractual requirement to remediate the land in accordance with the Technical Manual prior to commencement of any construction works OR remediation of the land as required by the Technical Manual is a condition of the Development Approval and/or Occupancy Certificate; and
| x | x | x | x | x | x | x | 2007-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | CIR Ruling | 7 | - The extent of the site addressed by the contractual requirement is justified and referenced consistently throughout the submission. NB: This Ruling does not apply to Green Star – As Built submissions and the site must have been fully remediated prior to assessment in strict accordance with the Technical Manual.
| x | [6 empty] | 2008-01-01 |  | Eco-3 |  |  | Reclaimed Contaminated Land | Technical Clarification | 8 | The Credit Criteria must be met prior to construction completion (and in accordance with the relevant regulation, as stipulated); 'completion.' should be inserted at the end of the first sentence of the Credit Criteria.
| x | x | x | x | x | x | x | 2008-09-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 9 | Significant Contamination is defined as any contamination (regardless of extent, concentration, toxicity, or otherwise) requiring remediation as determined by the relevant Federal, State or Local Authorities. In New South Wales, this determination would generally be made by the Local Council, which would refer to the Environmental Protection Agency’s State Environmental Planning Policy No 55 — Remediation of Land (SEPP 55) to make its decision. http://www.legislation.nsw.gov.au/viewtop/inforce/epi+520+1998+first+0+N Each state has different legislation determining what significant contamination is. See GBCA Technical Clarification No.11 dated December 2008 for further information.
| x | x | x | x | x | x | x | 2008-10-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Correction | 10 | Applies to all projects registered from November 2008 Where the Credit is ‘Not Applicable’, the following documentation is required: - Short report: Stating that the site contained buildings at the time of purchase and that they were retained and refurbished. - Evidence of site purchase: Clearly indicating the site, purchase date and any relevant site attributes. - Site documentation: Scaled site plans (with built area and GFA quantified) or aerial photographs generated at, or prior to, site purchase, showing the built area on the site.
| x | x | x | x | x | x | x | 2008-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 11 | Contamination is defined in the National Environment Protection Measure (NEPM) for the Assessment of Site Contamination, as “the condition of land or water where any chemical substance or waste has been added at above background level, and represents, or potentially represents, an adverse health or environmental impact”. While the NEPM for the Assessment of Site Contamination is a nationally consistent approach to assessing site contamination, each state and territory regulates the assessment of site contamination separately. The GBCA uses the term ‘significant contamination’ to refer to any contamination (regardless of extent, concentration, toxicity, or otherwise) requiring remediation as determined by the relevant federal, state or local authorities. To determine whether or not your project site requires remediation, refer to your state’s policies for implementing NEPM for the Assessment of Site Contamination. The links below may be useful for locating state-based information. National Standard: NEPM for the Assessment of Site Contamination
| x | x | x | x | x | x | x | 2008-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 11 | The National Environment Protection Measure (NEPM) for the Assessment of Site Contamination establishes a “nationally-consistent approach to the assessment of site contamination to ensure sound environmental management practices by the community which includes regulators, site assessors, contaminated land auditors, land owners, developers and industry”: http://www.ephc.gov.au/nepms/cs/con_sites.html ACT Territory and Municipal Services’ Contaminated Sites website: http://www.tams.act.gov.au/work/environment_for_business_and_industry/contaminatedsites NSW Department of Environment and Climate Change’s Contaminated Land website: http://www.environment.nsw.gov.au/clm/ NT Environment Heritage and the Arts Division of the Department of Natural Resources, Environment, The Arts and Sport’s website: http://www.nt.gov.au/nreta/environment/waste/contaminated.html http://portal.environment.wa.gov.au/portal/page?_pageid=53,34343&_dad=portal&_schema=PORTAL
| x | x | x | x | x | x | x | 2008-12-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Technical Clarification | 11 | QLD Environmental Protection Agency’s Contaminated Land website: http://www.epa.qld.gov.au/environmental_management/land/contaminated_land/#gen1 SA Environmental Protection Authority’s Site Contamination website: http://www.epa.sa.gov.au/contamination.html TAS Department of Environment, Parks, Heritage and the Arts Environment Division’s Land Contamination website: http://www.environment.tas.gov.au/land_contamination.html VIC Environment Protection Authority’s Land website: http://www.epa.vic.gov.au/land/default.asp WA Department of Environment and Conservation’s Contaminated Sites Database:
| x | x | x | x | x | x | x | 2011-01-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Correction | 12 | Documentation for this credit requires confirmation that site decontamination has been completed prior to the start of construction works. However, in some cases, construction works may be required to facilitate site decontamination works, e.g. Early shoring and foundation piling works. In these cases construction will start prior to site decontamination. For this to be deemed acceptable, a report must be submitted, explaining why early construction works were required.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Evidence of site purchase. *Extract(s) from the specification(s) -OR- Extract(s) from the main building contract -OR- Certificate from the Environmental Auditor. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Evidence of site purchase. All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | x | x | x | x | 2013-11-01 |  | Eco-3 | Eco-3 | Eco-3 | Reclaimed Contaminated Land | Documentation (As Built) | C | For As Built projects This credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x |  |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value
| x | [6 empty] | 2006-01-01 |  | Eco-4 |  |  | Change of Ecological Value | Withdrawn | 1 | See clarification Eco-4/2 It is indeed possible to achieve more than one point in the calculator. However, this would require substantial initiatives to make the site 'better than you found it' (e.g. green roofs, bio-swale blackwater treatment etc.). This credit is intended to challenge design teams to capture the synergy between the various project outcomes.
| x | [6 empty] | 2006-01-01 |  | Eco-4 |  |  | Change of Ecological Value | Technical Clarification | 2 | After considering feedback, the GBCA can confirm that it is possible to achieve more than one point in the calculator. However, this would require substantial initiatives to make the site 'better than you found it' (e.g. green roofs, bio-swale blackwater treatment). This credit is intended to challenge design teams to capture the synergy between the various project outcomes and the site. Overall, it must be understood that this Calculator is not designed as a landscaping tool but land use tool, and requires significant changes to the ecological value of the land for additional points to be gained.
| x | x | x | x | x | x | x | 2009-07-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Technical Clarification | 3 | Gravel can be inputed as 'Bare Ground' for the purposes of completing the Eco-4 Change in Ecological Value calculator.
|  | x | x | x | x | x | x | 2013-11-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Correction | 4 | The following Credit Criteria replaces that found within the Technical Manual for this credit: Where the threatened species requirement has been met, up to four points are awarded where as a result of the development, the ecological value of the site is either maintained or enhanced. The number of points awarded is determined by the Green Star - Change of Ecological Value Calculator based on a comparison of the state of the site before and after design/construction. Threatened species requirement: For Greenfield sites, the site has no threatened or vulnerable species and for reused sites (e.g. refurbishments), such species are adequately protected if present. Please refer to the Technical Manual, and previous rulings, for Documentation and Compliance Requirements.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Documentation (Design) | A | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Documentation (Design) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Construction architectural site plan. Projects must submit the following documentation instead: * Landscape plan(s) clearly identifying all land types present on the site in accordance with the Calculator and indicating the area they occupy. * Landscape schedule where planting and any requirements necessary to ensure that the landscaping functions as intended by the design are nominated. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Documentation (Design) | C | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Eco-4 | Eco-4 | Eco-4 | Change of Ecological Value | Documentation (As Built) | D | For purposes of this credit, the following documentation is to be provided in the General section of the submission and is no longer required to be submitted for this credit. * Site Documentation; * Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x |  |  |  |  | Eco-5 | Communal Garden Facilities
[8 empty] | 2008-09-01 |  |  |  | Eco-5 | Communal Garden Facilities | Technical Clarification | M1 | Definitions: 'Deep soil planting' would indicate a minimum depth of soil of 1500mm. 'Large tree' would indicate a tree which would be 15 metres or more at mature height.
[7 empty] | x | 2011-01-01 |  |  |  | Eco-5 | Communal Garden Facilities | Correction | 1 | The technical manual credit criteria: 'Playground Area' states: "…They must be sufficiently large to allow play by groups of up to 20 children, and...” This must be replaced with: “...at least 20 children, and...”.
x | [8 empty] | Eco-1 |  |  |  | Green Star - Office As Built Certified Building
x | [7 empty] | 2007-01-01 | Eco-1 |  |  |  | Green Star - Office As Built Certified Building | Technical Clarification | 1 | In order for a fitout to claim points, its base building must have been certified by the time of the Round 2 assessment at the latest; neither a Green Star - Office Design Certified Rating nor registration for Green Star - Office As Built will suffice. It is in the interest of the fitout to stay informed about the base building assessment process, and to coordinate the fitout submission after the base building submission has been reviewed.
x | [7 empty] | 2006-06-01 | Eco-1 |  |  |  | Green Star - Office As Built Certified Building | Technical Clarification | 2 | A Green Star - Office Design Certified Rating does not qualify a project for this credit. The Green Star - Office As Built assessment is undertaken after practical completion and validates that the commitments made in the design phase were carried through construction. In order for this credit to be claimed, the base building must have been certified under Green Star - Office As Built at the time of the fitout's submission.
x | [7 empty] | 2007-08-01 | Eco-1 |  |  |  | Green Star - Office As Built Certified Building | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem this credit 'Not Applicable' (na) due to the building being an existing building is denied because the credit aims to create an incentive for base building owners to achieve a Green Star rating for the completed development. However, in response to this CIR, the Credit Criteria has been expanded: compliance can also be achieved with a Green Star - Office Existing Building (PILOT or final) Certified Rating.
x | [8 empty] | Eco-2 |  |  |  | Building Layout Efficiency
x | [7 empty] | 2006-06-01 | Eco-2 |  |  |  | Building Layout Efficiency | Technical Clarification | 1 | If the tenancy fitout covers numerous floors, the BLE must be calculated as a total figure over all whole floors OR over all the floors of the building.
x | [7 empty] | 2006-06-01 | Eco-2 |  |  |  | Building Layout Efficiency | Technical Clarification | 2 | The perimeter atrium is considered a part of Core Structure.
x | [7 empty] | 2006-06-01 | Eco-2 |  |  |  | Building Layout Efficiency | Technical Clarification | 3 | The credit assesses the base building efficiency, NOT the efficiency of the furniture layout (i.e., how many people can be accommodated), hence for calculations, disregard the furniture layout and superimpose the required Primary Circulation, 1.5m wide (secondary and tertiary circulation are irrelevant), in the manner prescribed. All the measurements in the definition of Primary Circulation must be adhered to.
x | [8 empty] | Eco-3 |  |  |  | Building Environmental Management
x | [7 empty] | 2006-09-01 | Eco-3 |  |  |  | Building Environmental Management | Withdrawn | 1 | Withdrawn on 1-Nov-2013. Please refer to CIR Ruling 4. Where the lease is already in place, a separate contract between the tenant and the landlord is acceptable in place of the lease as stipulated in the Technical Manual. However, the submission would need to include evidence of contractual obligations, including penalty clauses, for the adherence to the requirements in Eco-3 and Eco-4.
x | [7 empty] | 2008-03-01 | Eco-3 |  |  |  | Building Environmental Management | Withdrawn | 2 | Withdrawn on 1-Nov-2013. Please refer to CIR Ruling 4. The Credit Interpretation Request (CIR) to provide an executed letter agreement instead of an extract from the Lease Agreement is granted conditionally on the project’s ability to provide a similar level of certainty and detail as that which would be found in the Lease Agreement. Please refer to the Technical Manual for mechanisms which may assist in providing this level of certainty.
x | [7 empty] | 2009-07-01 | Eco-3 |  |  |  | Building Environmental Management | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem a policy agreement between the facilities management and company CEO equivalent to a contractual agreement between the building owner and building management, where the building owner and building management are the same company, is granted conditionally. The policy agreement must demonstrate that the Credit Criteria will be met, and must be signed by both parties.
x | [7 empty] | 2013-11-01 | Eco-3 |  |  |  | Building Environmental Management | CIR Ruling | 4 | It is acceptable to provide evidence of the implementation of the environmental initiatives rewarded by this credit with the following types of documentation (in lieu of the documentation stipulated within the Technical Manual): • A contract between the tenant and the building management. The contract must require the landlord/ building manager to implement, manage and report on at least two environmental initiatives per the Credit Criteria and Additional Guidance. There is no requirement for this contract to contain penalty clauses. -OR- • An executed, countersigned, letter. The letter must detail the requirement of the building management to implement, manage and report on at least two environmental initiatives per the Credit Criteria and Additional Guidance. Where the project team pursues this through an executed counter signed letter, the letter must address the following: • Be addressed to one of the relevant parties (and written by the other); and • Be signed by both parties. Please note, there is no requirement for this executed letter agreement to contain penalty clauses.
x | [7 empty] | 2013-11-01 | Eco-3 |  |  |  | Building Environmental Management | Correction | 5 | Regardless of the approach used to demonstrate compliance with the credit, be it through a contract, lease or executed letter, there is no requirement to demonstrate the presence of penalty clauses.
x | [8 empty] | Eco-4 |  |  |  | Commitment to Building Performance
x | [7 empty] | 2008-03-01 | Eco-4 |  |  |  | Commitment to Building Performance | Withdrawn | 1 | Withdrawn on 1-Nov-2013. Please refer to CIR Ruling 3. The Credit Interpretation Request (CIR) to have an executed letter agreement detailing the roles and responsibilities of both parties with regards to the building owner / manager’s environmental initiatives be deemed equivalent to an extract from the Lease Agreement which contains this same information is granted conditionally on the project’s ability to provide a similar level of certainty and detail as that which would be found in the lease agreement. Please refer to the Technical Manual for mechanisms which may assist in providing this level of certainty.
x | [7 empty] | 2009-07-01 | Eco-4 |  |  |  | Commitment to Building Performance | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem a policy agreement between the facilities management and company CEO equivalent to a tenancy lease agreement between the building owner/management and the tenant, where the building owner and tenant are the same company, is granted conditionally. The policy agreement must demonstrate that the Credit Criteria will be met, and must be signed by both parties.
x | [7 empty] | 2013-11-01 | Eco-4 |  |  |  | Commitment to Building Performance | CIR Ruling | 3 | Project teams may to provide evidence of the implementation of the environmental initiatives rewarded by this credit with the following types of documentation (in lieu of the documentation stipulated within the Technical Manual): • An executed, countersigned, letter. The letter must detail the tenants requirement to comply with the building management's environmental initiatives per the Credit Criteria and Additional Guidance. Where the project team pursues this through an executed or counter-signed letter, the letter must address the following: • Be addressed to one of the relevant parties (and written by the other); and • Be signed by both parties. Please note, there is no requirement for this executed letter agreement to contain penalty clauses.
x | [7 empty] | 2013-11-01 | Eco-4 |  |  |  | Commitment to Building Performance | Correction | 4 | Regardless of the approach used to demonstrate compliance with the credit, be it through a contract, lease or executed letter, there is no requirement to demonstrate the presence of penalty clauses.
x | [8 empty] | Eco-5 |  |  |  | Shell and Core or Integrated Fitout
x | [7 empty] | 2007-08-01 | Eco-5 |  |  |  | Shell and Core or Integrated Fitout | Technical Clarification | 1 | While the Credit Criteria states “shell and core OR integrated fitout”, any combination of these is acceptable, i.e. areas delivered as shell-and-core and areas delivered as integrated fitout must jointly contribute the required proportion of the NLA.
x | [7 empty] | 2007-01-01 | Eco-5 |  |  |  | Shell and Core or Integrated Fitout | CIR Ruling | 2 | The installation of the raised floor system and the perimeter cell air conditioning displacement system is appropriate for Shell & Core project delivery as long as carpet tiles are not installed. If a tenant moves into a space newly fitted-out by the base building: A. The fitout will be deemed "an integrated fitout" for the purpose of this credit (to qualify for points) if the tenant accepts the fitout as is, i.e., undertakes no modification to 95% of the fitout. This solution is considered to demonstrate equivalent but alternative compliance with the Credit Criteria, as it delivers the same environmental outcome as an integrated fitout (i.e., no waste from re-fit). To confirm that 95% of the base building fitout has not been modified, please submit a report from the tenant detailing the modifications that took place (substantiated with "before" and "after" documentation, e.g. photographs or drawings, where appropriate), in addition to any other relevant documentation stipulated in the Technical Manual.
x | [7 empty] | 2007-01-01 | Eco-5 |  |  |  | Shell and Core or Integrated Fitout | CIR Ruling | 2 | Such a project can claim flooring as 'reused' in the Mat-2 'Flooring' Calculator. B. The fitout will not be deemed "an integrated fitout" for the purpose of this credit if the tenant modifies over 5% of the fitout. However, if any of the floor finish is retained, it can be deemed 'reused' for the purpose of Mat-2 'Flooring' to discourage unnecessary removal of new flooring.
x | [7 empty] | 2008-03-01 | Eco-5 |  |  |  | Shell and Core or Integrated Fitout | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem a previously occupied tenancy that has been stripped down to a shell and core status be deemed “shell and core” for purposes of Green Star – Office Interiors v1.1 is denied. As specified in the Technical Manual, this credit only applies to tenancy fitouts that are within a new base building construction or are part of an existing building refurbishment. All other building scenarios are considered ‘Not Applicable’ (na).
x | [7 empty] | 2009-03-01 | Eco-5 |  |  |  | Shell and Core or Integrated Fitout | Technical Clarification | 4 | Where the occupancy certificate does not show the required information for this credit or where the occupancy certificate is not available, it is acceptable for the project to provide letters from the tenant and owner, as follows: - A Letter from tenant outlining the tenancy requirements; and - A Letter from owner confirming that base building can adequately provide for the tenant requirements.
x | [8 empty] | Eco-6 |  |  |  | Building Conservation

## Emi (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Emissions
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Emi General | Emi General | Emi General | Emi General | General
| x | [6 empty] | 2008-01-01 |  | Emi-0 |  |  | General | Technical Clarification | 1 | It is understood that a number of different systems may be installed on a project. Whenever Emi-1 ‘Refrigerant ODP’ through Emi-4 Refrigerant Recovery’ are claimed, evidence must account for and describe all systems within the project. Where a system meets the Credit Criteria for Emi-1 ‘Refrigerant ODP’ and Emi-2 ‘Refrigerant GWP’, as documented in accordance with the Technical Manual, such system does not need to meet the requirements for Emi-3, and Emi-4.
x | x | x | x | x | x | x | x |  | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP
[8 empty] | 2008-01-01 |  |  |  | Emi-1 | Refrigerant ODP | Correction | M1 | A letter, from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
[5 empty] | x |  |  | 2011-01-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Correction | 1 | The technical manual requirements for this credit: 'Documentation: As Built' state: -"For naturally ventilated and mechanically assisted naturally ventilated spaces" This should be replaced with: -"Where refrigerants are present in the project".
x | x | x | x | x | x | x | x | 2013-11-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Technical Clarification | 2 | If all refrigerants on a project are Zero ODP then no information needs to be provided to state or confirm the volume of refrigerants. Please refer to the Technical Manual and Documentation rulings for all documentation requirements, this ruling does not impact on the type or number of documents which are required to be provided for this credit (only the content).
|  | x | x | x |  |  |  | 2009-03-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Documentation Guideline | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is claiming IEQ-1 'Ventilation Rates' by meeting the requirements for 'Naturally Ventilated Spaces' this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  | x | x | x | x | x | x | 2009-03-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Extracts from the O&M Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Documentation (Design) | B | Projects can substitute Extract(s) from the Specification(s) with Tender Drawings, or, an Equipment Schedule provided that the information required by the Technical Manual can be found within.
x | x | x | x | x | x |  | x | 2013-11-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Documentation (As Built) | C | Based on feedback from assessors and project teams the following documentation is no longer required for Green Star (As-Built Submissions): *Confirmation from contractor *Extracts from the commissioning report
x | x | x | x | x | x | x | x | 2013-11-01 | Emi-1 | Emi-1 | Emi-1 | Emi-1 | Refrigerant ODP | Documentation (As Built) | D | The following refrigerants are acknowledged as being Zero ODP: R-134a, R-125, R404A, R407B, R407C, R-410A, R-413A, R-507, HC-290, HC-600, HC-600a, R-717, R-744, R-1270. As such, wherever these refrigerants are used there is no requirement for the confirmation from the suppliers to include evidence that the refrigeratns have an ODP of zero. All other evidence must be provided as per the Technical Manual and other rulings. Please refer to the Technical Manual and rulings for all other documentation requirements, this ruling removes the requirement to provide documentation confirming the ODP of the above listed refrigerants only.
| x | x | x | x | x | x | x |  |  | Emi-2 | Emi-2 | Emi-2 | Refrigerant GWP
[8 empty] | 2008-01-01 |  |  |  | Emi-1 | Refrigerant ODP | Correction | M1 | A letter, from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
| x | x | x | x | x |  | x | 2011-01-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection | Technical Clarification | 1 | The credit criteria apply to all HVAC systems that service the project. This includes newly installed systems as well as existing systems. This includes shared systems as well as centralised systems.
|  | x | x | x |  |  |  | 2009-03-01 |  | Emi-2 | Emi-2 | Emi-2 | Refrigerant GWP | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is claiming IEQ-1 'Ventilation Rates' by meeting the requirements for 'Naturally Ventilated Spaces' this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-2 | Emi-2 | Emi-2 | Refrigerant GWP | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Extracts from the O&M Manual. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-2 | Emi-2 | Emi-2 | Refrigerant GWP | Documentation (Design) | B | Projects can substitute Extract(s) from the Specification(s) with Tender Drawings, or, an Equipment Schedule provided that the information required by the Technical Manual can be found within.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-2 | Emi-2 | Emi-2 | Refrigerant GWP | Documentation (As Built) | C | Projects can substitute As-built schematic mechanical drawing(s) with As Built Drawings, or, an As Built Equipment Schedule provided that all the information required by the Technical Manual can be found within.
| x | x | x | x | x | x | x |  |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection
| x | [6 empty] | 2007-01-01 |  | Emi-3 |  |  | Refrigerant Leaks / Refrigerant Leak Detection | Technical Clarification | 1 | Plant rooms must be ventilated to comply with the Building Code of Australia, and this requirement must continue to be met in buildings with refrigerant detection systems. The Credit Criteria stipulates a "moderately air-tight enclosure" must also be provided, so that the concentration of leaked refrigerant can build up to a detectable level. In order to demonstrate the refrigerant detection system will be effective, please clearly demonstrate the location of sensor points and ventilation openings and confirm that small refrigerant leaks will be detected, i.e. that the location, size and intended operation of the sensors and openings will not prevent that.
x | x | [6 empty] | 2008-01-01 | Emi-1 | Emi-3 |  |  | Refrigerant Leaks / Refrigerant Leak Detection | CIR Ruling | 2 | The Credit Interpretation Request (CIR) to deem an R123 system inherently sufficient for meeting the Aim of the credit because the system is under negative pressure when operating is denied. The Aim of Credit is to detect any leaks of refrigerant from the vessel at any time, including those that occur when the system is not in operation.
[8 empty] | 2008-01-01 |  |  |  | Emi-3 | Refrigerant Leaks | Correction | M1 | A letter, from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
| x | x | x | x | x | x | x | 2008-12-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection | Technical Clarification | 3 | Small packaged units do not need to be fitted out with a leak detection system or a refrigerant recovery system as per the credit criteria for this credit if the total sum of refrigerants for these units is not more than 5% of the total refrigerant volume of the project. Where the exclusion is being claimed, a tabulated summary demonstrating that 100% of all refrigerants in the project have been accounted for must be provided at the time of submission. Small packaged units must still comply with the credit criteria for Emi-1 and Emi-2.
| x | [6 empty] | 2009-05-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leak / Refrigerant Leak Detection | CIR Ruling | 4 | The CIR to deem the specification of a refrigerant leak detection system compliant with AS 1677.2 as meeting the requirements of Emi-3 for Green Star – Office v2 is granted conditionally upon the project’s ability to provide the following documentation: - Extracts from an O&M Manual; - For construction drawing showing HVAC system enclosures; - Refrigerant leak detection system drawings; and - Extract from the specification demonstrating the system’s compliance with AS 1677.2. In addition, all other requirements of the Technical Manual must be adhered to including the requirement for the specification of permanently installed multi-point sensing detectors.
|  | x | x | x |  |  |  | 2009-03-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is claiming IEQ-1 'Ventilation Rates' by meeting the requirements for 'Naturally Ventilated Spaces' this credit is 'Not Applicable' and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', these Deemed-to-Satisfy criteria shall not apply.
|  | x | x | x | x | x |  | 2009-03-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection | DTS | DTS-R | Based on feedback from the assessors and project teams, where refrigerants used in the project meet Emi-1 and Emi-2 the following documentation is no longer required: * Short Report * Tender Schematic Mechanical Drawings * Extract(s) from the specification (s) * Extract(s) from the O&M Manual. Projects must submit the following documentation instead * Confirmation from the mechanical engineer that all refrigerants used meet the requirements of Emi-1 'Refrigerant ODP' and Emi-2 'Refrigerant GWP'. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-3 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Leak Detection | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: For mechanically air-conditioned spaces: * Tender schematic mechanical drawings. Where the additional point is claimed: * Tender schematic mechanical drawings Projects must submit the following documentation instead: * Tender drawings of the HVAC system(s), indicating location and type of all elements containing refrigerant and showing the enclosure around each of the HVAC systems containing refrigerants, with the location, size and intended operation of the sensors and openings identified, and indicating the air-tightness of the space. All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | x | x | x | x |  |  | Emi-4 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Recovery
| x | [6 empty] | 2008-09-01 |  | Emi-4 |  |  | Refrigerant Leaks / Refrigerant Recovery | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to deem an automatic refrigerant pump-down system that can detect a leak via a leak detection system and can automatically pump down the refrigerant from the unit, store it in the condenser and contain it via the use of isolation valve(s), equivalent to pumping down the refrigerant to a storage tank or heat exchanger is granted.
| x | x | x | x | x | x | x | 2008-12-01 |  | Emi-4 | Emi-3 | Emi-3 | Refrigerant Leaks / Refrigerant Recovery | Technical Clarification | 2 | Small packaged units do not need to be fitted out with a leak detection system or a refrigerant recovery system as per the credit criteria for this credit if the total sum of refrigerants for these units is not more than 5% of the total refrigerant volume of the project. Where the exclusion is being claimed, a tabulated summary demonstrating that 100% of all refrigerants in the project have been accounted for must be provided at the time of submission. Small packaged units must still comply with the credit criteria for Emi-1 and Emi-2.
x | x | x | x | x | x | x | x |  | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP
| x | [6 empty] | 2007-08-01 |  | Emi-9 |  |  | Insulant ODP | Technical Clarification | 1 | It must be demonstrated that the specification of thermal insulation avoids the use of ozone depleting substances in both its manufacture and composition.
| x | x | x | x | x | x | x | 2007-08-01 |  | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Technical Clarification | 2 | Refurbishment projects ONLY: Any insulation which is already in place and which is not being touched, altered or refurbished is excluded from the calculations.
| x | [6 empty] | 2008-10-01 |  | Emi-9 |  |  | Insulant ODP | Technical Clarification | 3 | As stated in the Additional Guidance of this credit, this credit looks at the insulation of building services and building fabric. As such, in order to claim this credit, projects must submit the relevant sections of the architectural or façade specifications and all the applicable services specifications where insulation is commonly specified (i.e. mechanical, electrical, fire, hydraulics).
|  | x | x | x | x | x | x | 2008-10-01 |  |  | Emi-4 | Emi-4 | Insulant ODP | Technical Clarification | 4 | This Credit looks at the insulation of building services and building fabric. As such, in order to claim this credit, projects must submit the relevant sections of the Architectural or Façade Specifications and all the applicable services specifications where insulation is commonly specified (i.e. mechanical, electrical, fire, hydraulics).
x | x | x | x | x | x | x | x | 2009-04-01 | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Technical Clarification | 5 | To assist the assessment process, the following documentation should be provided in the Cover Sheet, or as a Short Report, at the time of submission: *Summary table listing all the insulation uses, the type and the ODP. The summary table must show where this item has been listed in each specification.
x | x | x | x | x | x | x | x | 2009-10-01 | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Technical Clarification | 6 | Where there are no thermal insulants used, the project can provide a letter from a suitably qualified person (e.g. mechanical engineer) rather than the extracts from the mechanical specification.
| x | x | x | x | x |  | x | 2011-01-01 | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Correction | 7 | This credit addresses all materials used for thermal insulation. Some materials may have acoustic insulation properties as well as thermal insulation properties. These dual purpose insulants must be included in the scope of this credit.
|  | x | x | x | x | x | x | 2009-03-01 | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Documentation (As Built) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: * Confirmation from the contractor. Furthermore, the following documentation is being modified to now read: * Confirmation from the supplier(s) - Identifying (with supporting evidence such as Manufacturer’s Data Sheets (MDS) and delivery docket(s) the type, and properties of the insulant(s) supplied to the project. - The MDS must clearly confirm that the insulants are free of ozone-depleting substances in both manufacture and composition. And, to assist the assessment process, the following documentation must be provided, in the cover letter, or as a Short Report, at the time of submission. *Summary table listing all the insulation uses, the type and the ODP. The summary table must show where in each specification this item has been listed. All other documentation must be provided as per the Technical Manual at the time of submission. All registered projects can provide the documentation stated in the Technical Manual, or the documentation as per this clarification.
x | x | x | x | x | x | x | x | 2013-11-01 | Emi-2 | Emi-9 | Emi-4 | Emi-4 | Insulant ODP | Documentation | B | Based on feedback from assessors and project teams, the following documentation is no longer required: Design rating: - Extract(s) from the specification(s) As Built rating: - Confirmation from the supplier(s) - Confirmation from the contractor Projects (both Design and As Built) must submit the following documentation instead: - A letter from the project's GSAP confirming compliance with the Credit Criteria.
| x | x | x | x | x | x | x |  |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution
| x x x | x | x | x | x | x | x | 2011-01-01 |  | Emi-5 | Emi-5 | Emi-5 | Please note there is a revised version of this credit called 'Stormwater' which was released on 01/01/2011. If your project was registered after 01/01/2011, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/emi-5-stormwater-credit/3496.htm
| x | [6 empty] | 2008-01-01 |  | Emi-5 |  |  | Watercourse Pollution | CIR Ruling | 1 | The Credit Interpretation Request (CIR) to use a shared blackwater treatment facility is granted on the basis that a suitably qualified professional has indicated that it is sized sufficiently to serve all nominated uses. Please refer to the ‘Interdependent Projects’ clarification located within the General section.
| x | x | x | x | x | x | x | 2008-03-01 |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution | Technical Clarification | 2 | The “Victorian EPA Best Practice for Environmental Management for Urban Stormwater” (1999) document has been published by CSIRO and is available to download from http://www.publish.csiro.au/nid/197/issue/3822.htm as a PDF document entitled “Urban Stormwater Best Practice Environmental Management Guidelines” (2006).
| x | x | x | x | x | x | x | 2008-12-01 |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution | Technical Clarification | 3 | The Victoria EPA Best Practice for Environmental Management for Urban Stormwater (1999) has been superseded by the CSIRO Urban Stormwater Best Practice Environmental Management Guidelines (2006); it is available at http://www.publish.csiro.au/nid/18/pid/2190.htm. Projects may use either guideline.
|  | x | x | x | x |  |  | 2011-01-01 |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution | Correction | 4 | To prove that the additional point for this credit is ‘Not Applicable’, the project must provide a statement from the project architect. This must confirm that the site does not contain a waterway and is not adjacent to a waterway. This evidence must be supported by site documentation presented in the 'General' section of the submission.
[8 empty] | 2008-09-01 |  |  |  | Emi-6 | Watercourse Pollution | Technical Clarification | M1 | To claim the additional point, the site boundary must be within 9 meters of a waterway or natural watercourse. Projects must ensure that all other requirements of the Credit Criteria have been adhered to when claiming points for this credit.
| x | x | x | x | x | x | x | 2012-08-01 |  | Emi-5 | Emi-5 | Emi-5 | Stormwater | Technical Clarification | 6 | The following is interim guidance for the modelling of Free Oils and Total Petroleum Hydrocarbons in demonstrating compliance with the pollution reduction targets in Emi-5 Stormwater: The latest version of the MUSIC software (v5) allows for the modelling of alternate constituents (beyond TN,TP,TSS and gross pollutants). Following feedback from the software developers, it is advised that Total Suspended Solids (TSS) is used as a surrogate for Total Petroleum Hydrocarbons, but not for Free Oils. The requirement for modelling of Free Oils is temporarily withdrawn until a version of the software is released that allows modelling of Free Oils.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Site Documentation. *Evidence of Site Purchase. Where applicable, the Short Report must reference the documentation submitted in the General section of this credit. Projects must ensure that the information contained within the short report and the information submitted in the general section is clear, consistent, and properly referenced. All other documentation must be provided as per the Technical Manual at the time of submission.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-5 | Emi-5 | Emi-5 | Watercourse Pollution | Documentation (As Built) | B | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Site Documentation. *Evidence of Site Purchase.
| x | x | x | x | x | x | x |  |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer
| x | [6 empty] | 2007-12-01 |  | Emi-6 |  |  | Reduced Flow to Sewer | Technical Clarification | 1 | The Green Building Council strongly supports the use of shared/centralised energy or treatment facilities and commends the project on employing this strategy. Both Wat-1 'Occupant Amenity Potable Water Efficiency' and Emi-6 'Reduced Flow to Sewer' can be achieved with a shared plant.
| x | x | x | x | x | x | x | 2008-01-01 |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer | Technical Clarification | 2 | It is understood that in many cases, the relevant Authority will not grant approval of the water reuse/recycling systems until they have been commissioned. For a Green Star Design submission it is acceptable to provide the authority’s preliminary approval, or if no objection to the system(s) by the authority, the documented design of the system(s) on the basis of relevant state and local standards. The authority must confirm that it is only able to approve operational systems. The authority’s subsequent approval of the operation system(s) may be conditional on the project’s ability to clearly demonstrate compliance with relevant regulation or standards, which may be cited. The relevant authority’s approval of the operational system(s) will still be necessary to confirm compliance for a Green Star As Built submission.
| x | x | x | x | x | x | x | 2008-08-01 |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer | Technical Clarification | 2 | Where the authority cannot provide approval, preliminary approval, or objections to the system at the time of submission, and where the authority has a set of published guidelines stating the requirements for a blackwater system, then the following must be provided instead: - Confirmation from the authority that neither approval, nor preliminary approval, nor objections to the system can be provided at this stage; - Confirmation from the hydraulics engineer engaged in the project stating that the blackwater system meets the published guidelines; - Extracts from the authority’s published guidelines that state the relevant criteria applicable to this project. The relevant passages must be highlighted; and - The cover letter/Short Report (required in the Technical Manual) from the hydraulics engineer must include a clear comparison showing how the system meets the criteria outlined in the authority’s published guidelines.
| x | x | x | x | x | x | x | 2008-08-01 |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer | CIR Ruling | 3 | The Credit Interpretation Request (CIR) to deem the approval of a test plant equivalent to the preliminary approval of the system for a Green Star submission is granted conditionally. Please note the following: The GBCA accepts that preliminary approval of a ‘test system’ (defined as a test of the full system) within a building is sufficient. However, the relevant Authority must confirm that if the test is successful, then there would be no objection to the ongoing use of the final system within the building. The project will need to provide confirmation from the approval Authority stating that it will only approve the operational system after testing, as per the above Technical Clarification. All other documentation required by the Technical Manual must be provided for as per the Wat-1/Emi-6 credits.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer | DTS | DTS-W | Based on feedback from the assessors and project teams, where no water treatment systems have been previously specified in the Wat-1 credit, only the calculator needs to be shown at the time of submission, provided that no additional uses or systems are being used in the building to meet this credit.
|  | x | x | x | x | x | x | 2009-03-01 |  | Emi-6 | Emi-6 | Emi-6 | Reduced Flow to Sewer / Discharge to Sewer | Documentation (Design) | A | Based on feedback from the assessors and project teams, where the additional point is claimed the following documentation is no longer required: * Blackwater Treatment Maintenance Plan. * Copy of the Maintenance plan. Projects must submit the following documentation instead: * Confirmation from the building owner stating that they are aware of the maintenance costs for this system, and that the costs have been budgeted for. All other documentation must be provided as per the Technical Manual at the time of submission.
| x | x | x | x | x | x | x |  |  | Emi-7 | Emi-7 | Emi-7 | Light Pollution
| x | x | x | x |  |  | x | 2011-01-01 |  | Emi-7 | Emi-7 | Emi-7 | Light Pollution | Correction | 1 | The following credit criteria is acceptable as an alternative to the credit criteria described in the technical manual: One point is awarded where: - No external luminaire has an upward light output ratio that exceeds 5%; - The lighting design complies with AS4282 ‘Control of the Obtrusive Effects of Outdoor Lighting’. Definition of 'Upward light output ratio' as per AS1158.0:2005: The ratio of the luminous flux emitted by a luminaire above the horizontal to that emitted by the lamp.
|  | x | x | x |  |  |  | 2009-03-01 |  | Emi-7 | Emi-7 | Emi-7 | Light Pollution | Documentation (Design) | A | The below documentation guideline can only be used in conjunction with Emi-7 Technical Clarification No. 1 Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: *Extracts from the specification(s). Furthermore, the following documentation is being modified to now read: * Short report from the lighting engineer describing how the Credit Criteria have been met by: - Detailing the external and atrium lighting on the site, the areas illuminated, calculations and illumination diagrams (including horizontal and vertical light distribution), and referencing the photometric data included in the luminaire schedule to demonstrate that no light spill is impacting the night sky or neighbouring properties in accordance with AS4282 1997. * Luminaire Schedule for all external lighting (and lighting within glazed atria where applicable), nominating the type, lighting distribution and quantity of each luminaire and including the relevant photometric data showing that the luminaires do not have an upward light output ratio that exceeds 5%. All other documentation must be provided as per the technical manual at the time of submission.
|  | x | x | x |  |  |  | 2009-03-01 |  | Emi-7 | Emi-7 | Emi-7 | Light Pollution | Documentation (As Built) | B | The below documentation guideline can only be used in conjunction with Emi-7 Technical Clarification No. 1 Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - As Built submission for this credit: *Confirmation from the contractor. Furthermore, the following documentation is being modified to now read: * Short report from the lighting engineer describing how the Credit Criteria have been met by: - Detailing the external and atrium lighting on the site, the areas illuminated, calculations and illumination diagrams (including horizontal and vertical light distribution), and referencing the photometric data included in the luminaire schedule to demonstrate that no light spill is impacting the night sky or neighbouring properties in accordance with AS4282 1997. * Luminaire Schedule for all external lighting (and lighting within glazed atria where applicable), nominating the type, lighting distribution and quantity of each luminaire and including the relevant photometric data showing that the luminaires do not have an upward light output ratio that exceeds 5%. All other documentation must be provided as per the technical manual at the time of submission.
| x | x | x | x | x | x | x |  |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers
| x x x | x | x | x |  |  |  | 2008-12-18 |  | Emi-8 | Emi-8 | Emi-8 | Please note there is a revised version of this credit called 'Legionella' which was released on 18/12/2008. If your project was registered after 18/12/2008, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/emi-8-cooling-towers-emi-8-legionella/1870.htm
| x | x | x | x | x |  | x | 2008-12-01 |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers | Correction | 1 | This credit has been revised as per the criteria set out in the following link: http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/emi-8-cooling-towers-emi-8-legionella/1870.htm Projects registered prior to December 2008 can choose to use this new criteria or the previous version of this credit. Projects registered after the 18th of December can only use the new version of this credit.
[8 empty] | 2009-02-01 |  |  |  | Emi-8 | Legionella / Cooling Towers | Correction | M1 | A letter, from the mechanical engineer or building owner, confirming that no air-conditioning equipment has been designed, or installed as part of the base building and the table of contents of the mechanical specifications will suffice to demonstrate compliance with this credit.
| x | x | x | x | x | x | x | 2013-11-01 |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers | Technical Clarification | 2 | This credit is limited to water based heat rejection systems. Evaporative coolers which cool air within the building, and do not form part of the heat rejection system for the buidling's HVAC, are not considered water based heat rejection systems for the purposed of this credit. Projects which only contain evaporative cooling systems can target points for this credit by providing the documentation outlined for ‘where there are no water-based heat rejection system serving the building(s)’.
| x | x | x | x | x | x | x | 2013-11-01 |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers | Technical Clarification | 3 | The GBCA confirms that combination wet/dry heat rejection systems which are combination of air-cooled chillers and evaporative cooling systems are to be treated as 'water based heat rejection systems' and documented within this credit accordingly. If the selected systems comply with the credit criteria for water based systems, then it will be possible to target a point for this credit using that compliance pathway. Please refer to the credit for all documentation and compliance requirements.
|  | x | x | x | x |  |  | 2009-03-01 |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers | DTS | DTS-NV | FOR NATURALLY VENTILATED PROJECTS ONLY For purposes of this credit, where the building is claiming IEQ-1 'Ventilation Rates' by meeting the requirements for 'Naturally Ventilated Spaces' this credit is automatically achieved and no documentation is required. Where this Deemed-to-Satisfy Criteria is claimed, projects must state within their cover sheet/short report that the project is claiming full points for IEQ-1 'Ventilation Rates'. Where the project does not achieve full points for IEQ-1 'Ventilation Rates', points will not be awarded for this credit.
|  | x | x | x | x |  | x | 2009-03-01 |  | Emi-8 | Emi-8 | Emi-8 | Legionella / Cooling Towers | Documentation (Design) | A | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star - Design submission for this credit: Where the building is air conditioned without water based heat rejection systems: * Extract(s) from the mechanical specifications. Where the building is air conditioned with water based heat rejection systems: * Extract(s) from the mechanical specifications.
[5 empty] | x | [6 empty] | Emi-9 | Trade Waste Pollution
[5 empty] | x |  |  | 2011-01-01 |  |  |  | Emi-9 | Trade Waste Pollution | Technical Clarification |  | For the purposes of this credit, the term 'effluent' denotes liquid that is flowing out of the site, into the sewerage system.
[6 empty] | x | [5 empty] | Emi-10 | Noise Pollution

## Inn (hidden)
x | x | x | x | x | x | x | x | Green Star Rulings
x | x | x | x | x | x | x | x | Innovation
x | x | x | x | x | x | x | x
[9 empty] | Office Interiors | Ov2 Numbering | Ov3 Numbering | New Tools Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M | Date | Credit | Credit | Credit | Credit | Title | Type | No. | Description | Comments
x | x | x | x | x | x | x | x |  | Inn-0 | Inn-0 | Inn-0 | Inn-0 | General
x | x | x | x | x | x | x | x |  | Inn-0 | Inn-0 | Inn-0 | Inn-0 | General
x | x | x | x | x | x | x | x |  | Inn-1 | Inn-1 | Inn-1 | Inn-1 | Innovative Strategies and Technologies
x x x | x | x | x | x | x | x | x | 2008-12-18 | Inn-1 | Inn-1 | Inn-1 | Inn-1 | Please note there is a revised version of this credit which was released on 15/09/2013. If your project was registered after 01/01/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/uploads/68/34884/Inn_1_-_Innovative_Strategies_and_Technologies_210813.pdf
x | x | x | x | x | x | x | x | 2011-01-01 | Inn-1 | Inn-1 | Inn-1 | Inn-1 | Innovative Strategies and Technologies | Technical Clarification | 1 | Eligibility to claim a tax credit from AusIndustry is not recognised by this credit. This credit assesses the pioneering nature of an initiative, in response to one of the following areas: - sustainable building design, sustainable building processes or advocacy for sustainable building. To demonstrate compliance, the following documentation must be provided: - An R&D plan that complies fully with AusIndustry 'Guidelines for Research and Development Plans 2001'. Financial data can be ommited from Green Star submissions for this credit. - Supporting documentation that provides evidence that the works described in the AusIndustry submission have been implemented. In the absence of an official R&D tax sign-off by AusIndustry, a short report must be provided as described in the technical manual. Green Star assessors will evaluate this report on the basis of the pioneering nature of the initiative and the resulting environmental benefits. Further information about claiming tax credits can be found at www.ausindustry.gov.au
x | x | x | x | x | x | x | x |  | Inn-2 | Inn-2 | Inn-2 | Inn-2 | Exceeding Green Star Benchmarks
x x x | x | x | x | x | x | x | x | 2008-12-18 | Inn-2 | Inn-2 | Inn-2 | Inn-2 | Please note there is a revised version of this credit which was released on 15/09/2013. If your project was registered after 01/01/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/uploads/68/34884/Inn_2_-_Exceeding_Green_Star_Benchmarks_210813.pdf
x | x | x | x | x | x | x | x | 2008-11-01 | Inn-2 | Inn-2 | Inn-2 | Inn-2 | Exceeding Green Star Benchmarks | Technical Clarification | 1 | Please note that where additional bicycle storage spaces are supplied, points under Inn-2 ‘Exceeding Green Star Benchmarks’ cannot be pursued unless ALL the cyclist facilities (including shower and changing facilities) are in par with the additional bicycle storage spaces provided.
x | x | x | x | x | x | x | x |  | Inn-3 | Inn-3 | Inn-3 | Inn-3 | Environmental Design Initiatives
x x x | x | x | x | x | x | x | x | 2008-12-18 | Inn-3 | Inn-3 | Inn-3 | Inn-3 | Please note there is a revised version of this credit which was released on 15/09/2013. If your project was registered after 01/01/2010, it is compulsory to use the revised credit. Please refer to the link below for more information. http://www.gbca.org.au/uploads/68/34884/Inn_3_-_Sustainable_Design_Initiatives_Updated.pdf
x | x | x | x | x | x | x | x |  | Inn-3 | Inn-3 | Inn-3 | Inn-3 | Environmental Design Initiatives
x

## Fitout VOC Limits (hidden)
x |  |  |  | x | x |  |  |  | Green Star Rulings
x |  |  |  | x | x |  |  |  | Indoor Environment Quality
x |  |  |  | x | x
OI |  |  |  | E | H |  |  |  | Credit | Title | Type | No. | Description
x |  |  |  | x | x |  |  | 2005-01-01 | IEQ-11 | Volatile Organic Compounds | Table | 1 | Internationally Accepted Test Methods
x |  |  |  | x | x |  |  | 2005-01-01 |  | The testing methods for tenancy fitout items have been expanded to include both small chamber and large chamber protocols. The product(s) must comply with the maximum TVOC limits in the IEQ-11 Table tab in this spreadsheet.
x |  |  |  | x | x |  |  | 2005-01-01
x |  |  |  | x | x |  |  | 2005-01-01
x |  |  |  | x | x |  |  | 2005-01-01 |  | Internationally Accepted Test Method | Small Chamber (typically used to report on product component emissions) | Large Chamber (typically used to report on entire finished item emissions)
x |  |  |  | x | x |  |  | 2005-01-01 |  | Testing Method | ASTM D5116-06 | ASTM 6670-01 OR US EPA Environmental Technology Verification (ETV) test method ‘Large Chamber Test Protocol for Measuring Emissions of VOCs and Aldehydes, September 1999’
x |  |  |  | x | x |  |  | 2005-01-01 | Fitout Items | Workstations | < 0.5 mg/item/h | < 0.5 mg/item/h
x |  |  |  | x | x |  |  | 2005-01-01 |  | Walls | < 0.5 mg/m2/h | < 0.5 mg/m2/h
x |  |  |  | x | x |  |  | 2005-01-01 |  | Partitions | < 0.5 mg/m2/h | < 0.5 mg/m2/h
x |  |  |  | x | x |  |  | 2005-01-01 |  | Tables | < 0.5 mg/item/h | < 0.5 mg/item/h
x |  |  |  | x | x |  |  | 2005-01-01 |  | Chairs | < 0.5 mg/item/h | < 0.5 mg/item/h
x |  |  |  | x | x |  |  | 2005-01-01 |  | Storage Units | < 0.5 mg/item/h | < 0.5 mg/item/h
x |  |  |  | x | x |  |  | 2005-01-01
x |  |  |  | x | x |  |  | 2005-01-01
| x | x | x |  |  | x | x | 2005-01-01 |  | This table is not applicable to this tool
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01
2005-01-01

## Ene-1 Table (hidden)
x | [8 empty] | Green Star Rulings
x | [8 empty] | Energy Efficiency
x
OI | [9 empty] | Credit | Title | Type | No. | Description
x | [7 empty] | 2005-01-01 |  | Ene-1 | Energy Efficiency | Table | 1 | Peripheral Allowance
x x x | [7 empty] | 2005-01-01 |  |  | Projects may use actual values for the peripheral loads in the ABGR Validation Protocol for Tenancies formula if they demonstrate (via a schedule with supporting documentation) that their peripheral loads are less than the normalized 80 w/person. The rest of the values used for the estimation must be as per the current AGBR Validation Protocol for Tenancies. In the Validation Protocol, the default allowance for peripherals of 80W per PC should be subtracted from the default allowances for standard office equipment.
x x x x x | [7 empty] | 2005-01-01 |  |  | Case |  | Default Equipment Load per Desk (80W peripheral load included): | Equipment Load per Desk if actual peripheral loads are calculated and used:
x | [7 empty] | 2005-01-01 |  |  | Standard office equipment, unknown screen type OR with all CRT screens |  | 220W | 140W + actual peripheral load
x | [7 empty] | 2005-01-01 |  |  | Standard office equipment, with all LCD screens |  | 190W | 110W + actual peripheral load
x | [7 empty] | 2005-01-01 |  |  | Standard office equipment, with all laptops |  | 100W | 20W + actual peripheral load
x | [7 empty] | 2005-01-01
x | [7 empty] | 2005-01-01
x | [7 empty] | 2005-01-01
| x | x | x | x | x | x | x | 2005-01-01 |  |  | This table is not applicable to this tool
x | [7 empty] | 2005-01-01
x | [7 empty] | 2005-01-01

## Dishwasher (hidden)
x | [6 empty] | x |  | Potable Water Efficiency Table
x | [6 empty] | x |  | Dishwasher Consumption
x | [6 empty] | x
OI | [6 empty] | M |  |  | Credit | Credit | Title | Type | No. | Description
x | [6 empty] | x | 2005-01-01 |  | Wat-1 | Wat-1 | Potable Water Efficiency | Table | 1 | Dishwasher consumption
x | [6 empty] | x | 2005-01-01 |  |  |  | Product | Units of Measurement | A | AA | AAA | AAAA | AAAAA
x | [6 empty] | x | 2005-01-01 |  |  |  | Dishwashers | Litres/place | >2 to 2.8 | >1.5 to 2 | >1 to 1.5 | >0.8 to 1 | 0.8 or less
x | [6 empty] | x | 2005-01-01
x | [6 empty] | x | 2005-01-01
x | [6 empty] | x | 2005-01-01
x | [6 empty] | x | 2005-01-01
| x | x | x | x | x | x |  | 2005-01-01 |  |  |  | This table is not applicable to this tool
x | [6 empty] | x | 2005-01-01
x | [6 empty] | x | 2005-01-01

## Chain of Custody (hidden)
x | x | x | x | x | x | x | x |  | FSC - Chain of Custody
x | x | x | x | x | x | x | x
x | x | x | x | x | x | x | x
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | Credit | Credit | Credit | Credit | Title | Type | No. | Description
x | x | x | x | x | x | x | x | 2005-01-01 |  | Mat-11 | Mat-8 | Mat-8 | Mat-7 | Sustainable Timber | WITHDRAWN | 1 | Chain of Custody Requirements
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | Chain-of-custody certification provides a guarantee about the production of FSC-certified products. Chain-of-custody is the path taken by raw materials from the forest to the consumer, including all successive stages of processing, transformation, manufacturing and distribution. Companies or individuals that process, transform, or trade (take ownership of) FSC certified forest products must be CoC certified. *The last person in the chain of ownership for materials being supplied to the construction project does NOT need to be CoC certified, but the company those materials are being received from does. The important issue here is ownership. For example, a spec contractor must be CoC certified as they will not be the final owner of the FSC materials.
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01
x | x | x | x | x | x | x | x | 2005-01-01 | [5 empty] | Industry Type | Process Stage |  | Chain-of-custody required?
x | x | x | x | x | x | x | x | 2005-01-01 | [5 empty] | Building & Construction | Sawmills, Lumberyards |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Manufacturers of forest products |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Timber brokers |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Artisans, carpenters |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Building contractors |  | NO*
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Retailers (i.e. DIY stores) |  | NO
x | x | x | x | x | x | x | x | 2005-01-01 | [5 empty] | Printing & Paper | Pulp, paper producer |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Paper merchant |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Broker |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Printers |  | YES
x | x | x | x | x | x | x | x | 2005-01-01 | [6 empty] | Publisher |  | NO
2005-01-01
2005-01-01
2005-01-01
2005-01-01

## Formaldehyde Emission Limits (hidden)
x | x | x | x | x | x | x | x |  | Green Star Rulings
x | x | x | x | x | x | x | x |  | Indoor Environment Quality
x | x | x | x | x | x | x | x
[10 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title | Type | No. | Description
| x | x | x | x | x | x | x | 2005-01-01 |  |  | IEQ-14 | IEQ-14 | IEQ-9 | Formaldehyde Emission Limits | Table | 1 | Formaldehyde Emission Limits
| x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x | 2005-01-01 | [5 empty] | The following table (IEQ-14.1) summarizes and clears up a number of clarifications on the existing spreadsheet. This table replaces all emission level tables for this credit released in: - Green Star - Office Design v1 - Green Star - Office As Built v1 - Green Star - Office Design v2 - Green Star - Office As Built v2 - Green Star - Office v3 - Green Star - Retail Centre v1 - Green Star - Office Interiors v1.1 - Green Star - Education v1 - Green Star - Healthcare Pilot - Green Star - Industrial Pilot - Green Star - Multi-Unit Residential Pilot All projects registered after 20/11/2008 must comply with this correction. All projects registered before this date have the following options: 1) Use the table below as per this technical clarification; or 2) Use the table in the current Technical Manual. Project teams cannot combine elements from both options to support their submission.
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | Test Protocol |  | Emission limit/ Unit of measurements
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | - AS/NZS 2269:2004, testing procedure AS/NZS 2098.11:2005 method 10 for Plywood |  | < 1.0 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | AS/NZS 1859.1:2004 - Particle Board, with use of testing procedure AS/NZS 4266.16:2004 method 16 |  | < 1.5 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | AS/NZS 1859.2:2004 - MDF, with use of testing procedure AS/NZS 4266.16:2004 method 16 |  | < 1.0 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | JIS A 5908:2003- Particle Board and Plywood, with use of testing procedure JIS A 1460 |  | < 1.0 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | JIS A 5905:2003 - MDF, with use of testing procedure JIS A 1460 |  | < 1.0 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | JIS A1901 (not applicable to Plywood) |  | < 1.0 mg/L
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | ASTM D5116 |  | <0.1 (+/- 0.0005) mg/m²hr (may also be represented as mg/m²/hr)
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | ISO 16000 part 9, 10 and 11 (also known as EN 13419) |  | <0.1 (+/- 0.0005) mg/m²hr (may also be represented as mg/m²/hr)
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | ASTM D6007 |  | 0.12mg/m³*
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | ASTM E1333 |  | 0.12mg/m³**
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | EN 717-1 (also known as DIN EN 717-1) |  | 0.12 mg/m³
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | EN 717-2 (also known as DIN EN 717-2) |  | 3.5 mg/m²hr (may also be represented as mg/m²/hr).
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | *The test report must confirm that the conditions of Table 1 comply for the particular wood product type, the final results must be presented in EN 717-1 equivalent (as presented in the table) using the correlation ratio of 0.98.
| x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | ** The final results must be presented in EN 717-1 equivalent (as presented in the table), using the correlation ratio of 0.98.
2005-01-01
x | [7 empty] | 2005-01-01 | [5 empty] | This table is not applicable to this tool
2005-01-01
2005-01-01

## OI IEQ-12 Formaldehyde (hidden)
x | x | x | x | x | x | x | x |  | Technical Clarifications Spreadsheet
x | x | x | x | x | x | x | x |  | Indoor Environment Quality
x | x | x | x | x | x | x | x
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title | Type | No. | Description
x x x | [9 empty] | IEQ-12 |  |  |  | Formaldehyde Emission Limits | Table | 1 | Emission limit values for 1 and 2 points applicable to IEQ-12.
x x x x x | [7 empty] | 2005-01-01 | [5 empty] | The following table (IEQ-12.2) resolves and summarises a number of clarifications on the acceptable test methods and emission limits for 1 and 2 points in the credit. This table replaces all emission level tables for this credit released in Green Star - Office interiors v1.1
x x | [7 empty] | 2005-01-01 | [5 empty] | Test Protocol |  | Emission Limit for 1 point | Emission limit for 2 points
x x x | [7 empty] | 2005-01-01 | [5 empty] | AS/NZS 2269:2004, testing procedure AS/NZS 2098.11:2005 method 10 for Plywood |  | ≤1mg/ L | ≤0.3mg/L (mean) and 0.4mg/L (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | AS/NZS 1859.1:2004 - Particle Board, with use of testing procedure AS/NZS 4266.16:2004 method 16 |  | ≤1.5 mg/L | ≤0.3mg/L (mean) and 0.4mg/L (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | AS/NZS 1859.2:2004 - MDF, with use of testing procedure AS/NZS 4266.16:2004 method 16 |  | ≤1mg/ L | ≤0.3mg/L (mean) and 0.4mg/L (max)
x x x x x | [7 empty] | 2005-01-01 | [5 empty] | JIS A 5908:2003- Particle Board and Plywood, with use of testing procedure JIS A 1460 (This test protocol is known as F**** [F4Star]) |  | ≤1mg/ L | ≤0.3mg/L (mean) and 0.4mg/L (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | JIS A 5905:2003 - MDF, with use of testing procedure JIS A 1460 |  | ≤1mg/ L | ≤0.3mg/L (mean) and 0.4mg/L (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | JIS A1901 (not applicable to Plywood) |  | ≤0.1 (+/- 0.0005) mg/m²hr* | ≤0.005 mg/m²hr
x x x | [7 empty] | 2005-01-01 | [5 empty] | ASTM D5116 |  | ≤0.1 (+/- 0.0005) mg/m²hr | ≤0.005 mg/m²hr
x x x | [7 empty] | 2005-01-01 | [5 empty] | ISO 16000 part 9, 10 and 11 (also known as EN 13419) |  | ≤0.1 (+/- 0.0005) mg/m²hr at 3 days | ≤0.005 mg/m²hr at 3 days
x x x | [7 empty] | 2005-01-01 | [5 empty] | ASTM D6007 |  | ≤0.12mg/m³** | ≤0.04 mg/m3* (mean) and 0.05mg/m3 (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | ASTM E1333 |  | ≤0.12mg/m³*** | ≤0.04 mg/m³*8 (mean) and 0.05mg/m3 (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | EN 717-1 (also known as DIN EN 717-1) |  | ≤0.12mg/m³ | ≤0.04 mg/m³ (mean) and 0.05mg/m3 (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | EN 717-2 (also known as DIN EN 717-2) |  | ≤3.5mg/m²hr | ≤0.11 mg/m²hr (mean) and 0.13mg/m²hr (max)
x x x | [7 empty] | 2005-01-01 | [5 empty] | * mg/m²hr may also be represented as mg/m²/hr
x x x | [7 empty] | 2005-01-01 | [5 empty] | ** The test report must confirm that the conditions of Table 1 comply for the particular wood product type, the final results must be presented in EN 717-1 equivalent (as presented in the table) using the correlation ratio of 0.98.
x x x | [7 empty] | 2005-01-01 | [5 empty] | *** The final results must be presented in EN 717-1 equivalent (as presented in the table), using the correlation ratio of 0.98.
x | [7 empty] | 2005-01-01
x | [7 empty] | 2005-01-01
x | [7 empty] | 2005-01-01
| x | x | x | x | x | x | x | 2005-01-01 | [5 empty] | This table is not applicable to this tool

## Paints & Adhesives (hidden)
x | x | x | x | x | x | x | x |  | Green Star Rulings
x | x | x | x | x | x | x | x |  | Indoor Environment Quality
x | x | x | x | x | x | x | x
[10 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title | Type | No.
x | x | x | x | x | x | x | x | 2005-01-01 |  | IEQ-11 | IEQ-13 | IEQ-13 | IEQ-8 | Maximum TVOC Content Limits for Paints, Varnishes and Protective Coatings | Table | 1
x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x | 2005-01-01 | [5 empty] | The tables in the Paints and Adhesives tab of this spreadsheet supersede the Paint and Adhesive & Sealant VOC Levels stipulated in the following Green Star rating tools. - Green Star - Office Design v2 - Green Star - Office As Built v2 - Green Star - Office Interiors v1.1 All Office v2 projects registered after 20/11/2008 must comply with this correction. All projects registered before this date have the following options: 1) Use the tables below as per this technical clarification; or 2) Use the tables in the current Technical Manual. Project teams cannot combine elements from both options to support their submission. For the tools listed below the only change is the addition of "Walls and Ceilings - interior gloss" to the Paints Table. All other values are identical: -Green Star - Office v3, -Green Star - Retail Centre v1 -Green Star - Education v1
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | PAINTS
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Product Type/Sub Category | Max TVOC content (g/l of ready-to-use product)
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Walls and ceilings - interior gloss | 75
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Walls and ceilings - interior semi gloss | 16
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Walls and ceilings - interior low sheen | 16
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Walls and ceilings - interior flat washable | 16
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Ceilings - interior flat | 14
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Trim - gloss, semi gloss, satin, varnishes and wood stains | 75
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Timber and binding primers * | 30
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Latex primer for galvanized iron and zincalume | 60
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Interior latex undercoat | 65
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Interior sealer | 65
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | One and two pack performance coatings for floors * | 140
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Any solvent-based coatings whose purpose is not covered in table | 200
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | Maximum TVOC Content Limits for Paints, Varnishes and Protective Coatings *EU Directive
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | ADHESIVES
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Product Type | Maximum TVOC content* (g/litre of product)
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Indoor carpet adhesive | 50
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Carpet pad adhesive | 50
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Wood flooring and Laminate adhesive | 100
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Rubber flooring adhesive | 60
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Sub-floor adhesive | 50
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Ceramic tile adhesive | 65
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Cove base adhesive | 50
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Dry Wall & Panel adhesive | 50
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Multipurpose construction adhesive* | 70
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Structural glazing adhesive | 100
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Architectural sealants* | 250
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01 | [5 empty] | Maximum TVOC limits for Adhesives & Sealants *Sealants used to enhance the fire- and water-proofing properties are included.
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01

## Public Transport DTS (hidden)
x | x | x | x | x | x | x | x |  | Green Star Rulings
x | x | x | x | x | x | x | x |  | Transport
x | x | x | x | x | x | x | x
[10 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title | [5 empty] | Type | No.
x | x | x | x | x | x | x | x | 2005-01-01 |  | Tra-1 | Tra-4 | Tra-4 | Tra-4 | Deemed to Satisfy Methodology | [5 empty] | Table | 1
x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | 2005-01-01 | [5 empty] | The following postal codes have been assessed against the Public/Mass Transport Calculator. Projects located within these postal regions and within 500m (walking distance) of either a bus interchange with at least six bays or a train station with at least four platforms will automatically receive 5 (five) points for this credit:
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Postal codes with a 'deemed to satisfy' provision
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | ACT | NSW | VIC | QLD | SA | WA | NT | TAS
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [6 empty] | 2000 | 3000 | 4000 | 5000
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [6 empty] | 2010 | 3008
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [6 empty] | 2060 | 3121
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [7 empty] | 3205
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Deemed to Satisfy - Documentation Requirements
X X x x x x x | X X x x x x x | X X x x x x x | X X x x x x x | X X x x x x x | X X x x x x x | X X x x x x x | X X x x x x x | 2005-01-01 | [5 empty] | Projects that meet the Deemed to Satisfy Criteria must submit the following documentation: • Confirmation from the Architect, Project Manager, ESD Consultant, OR Principal GS Accredited Professional stating that the project is in the relevant postcode, and within 500 meters (walking distance) of a transportation hub; and • A Site Plan OR a location map, both extending to the surrounding areas showing the walking distance from the major public entrance(s) of the building to the entrance of the transportation hub.
X X | X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | To have your postal code added to the Deem to Satisfy Criteria
X X x x x x | X X x x x x | X X x x x x | X X x x x x | X X x x x x | X X x x x x | X X x x x x | X X x x x x | 2005-01-01 | [5 empty] | If a project believes that a postal code qualifies as a ‘Deemed to Satisfy’, a Credit Interpretation Request (CIR) must be submitted to greenstar@gbcaus.org or your case manager, accompanied by a completed Transport Calculator, demonstrating that a transportation hub (defined as a bus interchange with at least six bays or a train station with at least four platforms) is within the project’s post code. Please note: A project will still need to show that it is within 500m walking distance from the transportation hub in order to claim the deemed to satisfy criteria.
x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | x x x x x x | 2005-01-01 | [5 empty] | If the project meets the criteria, then the postal code will be added to the deemed to satisfy provision table, whereby only the deemed to satisfy documentation will need to be submitted for a Green Star assessment. If the project does not meet the criteria, the project team may still able to claim full points for this Credit, however, the Compliance Requirements and Submission requirements of the Technical Manual must be met.
x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | 2005-01-01

## OI IEQ-14 Emission Limits (hidden)
x | x | x | x | x | x | x | x |  | Green Star Rulings
x | x | x | x | x | x | x | x |  | Indoor Environment Quality
x | x | x | x | x | x | x | x
[10 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title |  | Type | No.
x | [7 empty] | 2005-01-01 |  | IEQ-14 |  |  |  | IEQ-14 Emission Limits |  | Table | 1
x x x x x x x | [7 empty] | 2005-01-01 | [5 empty] | Individual printers placed outside a print/photocopy room (i.e. in the general office area), that are not grouped next to other printing equipment, and meet the emissions limits in the IEQ-14 Emission Limits when tested under the requirements of ECMA-328, can be excluded from this credit. Projects must submit test results showing that the selected equipment meets the relevant credit criteria. The test result must show that testing occurred as per ECMA-328.
X X | [7 empty] | 2005-01-01
X X | [7 empty] | 2005-01-01 | [5 empty] | Emission type Limit | (mg / h)
X X | [7 empty] | 2005-01-01 | [5 empty] | Dust | 4
X X | [7 empty] | 2005-01-01 | [5 empty] | Ozone | 2
X X | [7 empty] | 2005-01-01 | [5 empty] | Styrene | 1
X X | [7 empty] | 2005-01-01 | [5 empty] | Benzene | 0.1
X X | [7 empty] | 2005-01-01 | [5 empty] | TVOC Printing Emission Rate | 10
x x | [7 empty] | 2005-01-01 | [5 empty] | TVOC Ready Mode Rate | 1
x x | [7 empty] | 2005-01-01 | [5 empty] | TVOC Floor Mount Rate | 3
x x x | [7 empty] | 2005-01-01
| x | x | x | x | x | x | x | 2005-01-01 | [5 empty] | This table is not applicable to this tool

## GHG (hidden)
x | x | x | x | x | x | x | x | Technical Clarifications Spreadsheet
x | x | x | x | x | x | x | x | Energy
x | x | x | x | x | x | x | x
[9 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  | No. | No. | No. | No. | Title
|  | x x x x x x x x | [8 empty] | Ene |  | Green Star – Office v3: Approach to Greenhouse Gas Emissions This information can also be found at: http://www.gbca.org.au/uploads/174/1710/Green%20Star%20Fact%20Sheet%20-%20Approach%20to%20GHG%20Emissions%20in%20Energy.pdf
|  | x x x x x x x x x x x xx x x x x x | [10 empty] | There are two credits within Green Star – Office Design and Office As Built version 3 (v3) rating tools that directly target greenhouse gas emissions. These credits are the Ene-Conditional Requirement (Ene-CR) and Ene-1 ‘Greenhouse Gas Emissions’ (Ene-1). The key aim of Ene-CR and Ene-1 within Green Star is to reward reductions in the greenhouse gas emissions associated with buildings. To demonstrate compliance with these credits energy modelling is currently required. In Green Star – Office v3 the credit Ene-CR must be achieved for the project to be eligible for assessment and certification, whilst Ene-1 rewards predicted ‘net zero greenhouse gas emissions in operation’ with the maximum 20 points. Compliance with Ene-CR and Ene-1 can be achieved through two methods which are described below.
|  | x x x x x x x x x x x xx x | [10 empty] | METHODS FOR DETERMINING COMPLIANCE The first step in identifying the predicted greenhouse gas emissions for any building is to ascertain the predicted energy consumption used in the building, e.g. electricity (kWh/annum) and gas (MJ/annum). At present energy modelling must be carried out in accordance with the NABERS Energy Guide to Building Energy Estimation Modelling (located at www.nabers.com.au under ‘Resources’), in order to demonstrate compliance with Ene-CR and Ene-1. Currently projects can choose either of the alternative routes detailed below for demonstrating compliance with Ene-CR and Ene-1. Please refer to the explanations and diagram below for further details.
|  | x x x x x x x x x x x xx x x x x x x x x x | [10 empty] | Method: Using the NABERS Energy Guide to Building Energy Estimation Project teams are required to use the NABERS Energy Guide to Building Energy Estimation to carry out the energy modelling. Once modelling is complete and the predicted energy consumption for electricity (kWh/annum) and gas (MJ/annum) are known, there are two routes available to you. Route 1 Route 1 requires the project team to enter the predicted energy consumption for electricity (kWh/annum) and gas (MJ/annum) into the Green Star – Office v3 Energy Calculator (Energy Calculator). The Energy Calculator then calculates the project’s predicted greenhouse gas emissions (kgCO2e-/m2) figure and confirms automatically whether Ene-CR has been met and how many points have been achieved in Ene-1. Route 2 Route 2 allows the project team to use the predicted greenhouse gas emissions (kgCO2e-/m2) figure reported in the NABERS Energy Rating Calculator to demonstrate compliance with the Conditional Requirement and establish how many points the project has achieved in Ene-1.
|  | X X x x x x x x x x x x x x x x x | [11 empty] | 2000 | 3000 | 4000 | 5000
|  | X X x x x x x x | [10 empty] | The answer you get from the Green Star Energy Calculator may differ from the answer you get from the NABERS Energy Rating tool and may differ from the emissions in your NABERS Energy Pre-Commitment Agreement. This is as a result of the differences in approach of Green Star and NABERS in normalising for the differences in greenhouse gas coefficients and climates between the states of Australia. Projects are advised to use the most beneficial outcome from these calculations for assessment of greenhouse gas emissions under Green Star. | 2010 | 3008
|  | X X x x x x x x x x x x x x x x | [10 empty] | Data to be entered into the Green Star – Office v3 Energy Calculator The following guidance is provided to assist if you have chosen to use the Energy Calculator to demonstrate compliance with Ene-CR and Ene-1 as per Route 1 above. The following data is required to be entered in to the white cells of the Energy Calculator: 1. The location of the building (State); 2. The Net Lettable Area (NLA) of the building; and 3. The total predicted energy consumption of the buildingfor electricity (kWh/annum) and gas (MJ/annum). The Energy Calculator will then calculate the greenhouse gas emissions per square metre of NLA for the building (kgCO2e-/m2). This number is used to determine whether the building meets Ene-CR and how many points are allocated to the building for Ene-1. | 2060 | 3121
|  | X X x x x x x x x x x x x x x | [10 empty] | FUTURE DEVELOPMENTS FOR THE ENERGY CALCULATOR The Green Star – Office v3 Energy Calculator Guide A PILOT Green Star – Office v3 Energy Calculator Guide (Guide) has been produced as an alternative to using the NABERS Energy Guide to Building Energy Estimation to carry out the project’s energy modelling. This Guide is intended to be used alongside the Energy Calculator. This Guide will go through testing over the coming months before being available to download from the GBCA website for public comment in March 2009. Further details regarding the Guide will be published on the GBCA website and in the GBCA newsletter as they become available. |  | 3205
x x x
x | x |  | x | x | x | x | x | [5 empty] | This table is not applicable to this tool
Use the NABERS Energy Protocol for modelling
Enter kWh/annum
and MJ/annum into
Energy Calculator
Points will be
automatically
calculated by the
Energy Calculator
Use the normalised emissions
produced by the NABERS Energy
Rating tool (kgCO2e-/m2)
Points to be established manually
by comparing your project
against the Ene-1 benchmarks
OR

## Steel Calculation (hidden)
x | x | x | x | x | x | x | x |  | Technical Clarifications Spreadsheet
x | x | x | x | x | x | x | x |  | Materials
x | x | x | x | x | x | x | x
[10 empty] | Interiors Numbering | Ov2 Numbering | Ov3 Numbering | New Numbering
OI | Ov2 | Ov3 | RC | E | H | I | M |  |  | No. | No. | No. | No. | Title |  | Type |  | No.
| x | x | x | x | x | x | x | 2005-01-01 |  |  | Mat-6 | Mat-6 | Mat-5 | Steel / Recycled Content of Steel |  | Table |  | 1
| x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x | 2005-02-01 | [5 empty] | This correction applies to all projects registered after this date. Projects registered prior to this date can choose to submit as per the technical manual or as per this correction. There are two methodologies for demonstrating compliance: 1) Product by product The average post-consumer recycled content of steel in a project can be demonstrated on a product by product basis. The post-consumer recycled content of each product must be confirmed from the supplier. The percentage (by mass) of the products that meet the 50% post-consumer recycled content criteria should then be calculated. This percentage is then compared to the Credit criteria to determine how many Green Star points are awarded.
| x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | x x x x x x x x x x x x x x x x x x x x x x x x | 2005-02-01 | [5 empty] | 2) Overall percentage The average post-consumer recycled content of steel in a project can be demonstrated through calculating the percentage of (by mass) of post-consumer recycled steel used in the project. The overall percentage must be calculated using the following method: 1. Calculate the mass of post-consumer recycled content used in the project 2. Calculate the percentage (by mass) of all steel that is post-consumer recycled content 3. Compare the percentage to the Credit criteria to determine how many points can be claimed, as follows; A. One point can be claimed when the overall percentage of recycled content is 30% or more. This is deemed to be equivalent to 60% of the steel in the project having a recycled content of 50%. B. Two points can be claimed when the overall percentage of recycled content is 45% or more. This is deemed to be equivalent to 90% of the steel in the project having a recycled content of 50%. The following is an example of how the two different calculation methodologies are applied to a building where 1000 tonnes of steel is used:
| X x x x X | X x x x X | X x x x X | X x x x X | X x x x X | X x x x X | X x x x X | 2005-01-01 | [5 empty] | Type of steel | Mass (tones) | Post-consumer recycled content | Post-consumer recycled content more than 50% | Mass of post-consumer recycled content steel (tones)
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Reinforcement bar | 700 | 75% | Yes | 525
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Reinforcing mesh | 225 | 80% | Yes | 180
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Universal beams | 50 | 45% | No | 22.5
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Channels | 25 | 0% | No | 0
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Method 1: Product by product
| X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | 2005-01-01 | [5 empty] | 1) The type of steel used in the project that has a post-consumer recycled content of more than 50% are the reinforcement bar and the reinforcing mesh. 2) Combined, the mass of steel with post-consumer recycled content more than 50% is 925 tonnes. 3) The percentage of steel products that meet the criteria equals 92.5% (925 tonnes/1000 tonnes) Two points can be claimed in the credit, as 92.5% > 90%.
| X X | X X | X X | X X | X X | X X | X X | 2005-01-01 | [5 empty] | Method 2: Overall percentage
| X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | X X x x x x x x x x x | 2005-01-01 | [5 empty] | Following the numbered steps in the explanation above: 1. Calculate the mass of post-consumer recycled content used in the project: 525+180+22.5+0= 727.5 2. Calculate the percentage (by mass) of all steel that is post-consumer recycled content: 727.5/1000 = 73% 3. Compare the percentage to the Credit Criteria to determine how many points can be claimed. Two points can be claimed as 73% > 45%.
x | [7 empty] | 2005-01-01 | [5 empty] | This table is not applicable to this tool