## Green Star
The Green Building Council of Australia (GBCA) recommends that you use this rating tool in conjunction with the Green Star - Office Design v3 and Green Star - Office As Built v3 Technical Manual. To obtain a copy, please see www.gbcaus.org.
Green Star - Office Design v3 and Green Star - Office As Built v3 validates the environmental initiatives of the design phase of new office construction or base building refurbishment; or construction and procurement phase of a Class 5 office building.
You are invited to use Green Star - Office Design v3 and Green Star - Office As Built v3 to predict a Green Star rating. The GBCA does not endorse any self-assessed rating and you are forbidden from presenting self-assessment results in the public domain. The GBCA offers a formal certification process for ratings of Four Stars and above; this service provides for independent third party review of points claimed to ensure all points can be demonstrated to be achieved by the provision of the necessary documentary evidence. The use of Green Star - Office without formal certification by the GBCA does not entitle the user or any other party to promote a Green Star rating publicly.
To check for the latest release of a Green Star rating tool, please visit the GBCA website at: www.gbca.org.au. Details of changes made to each release of this tool can be viewed in the "Changelog" worksheet by clicking here. Green Star registered projects are permitted to use the release which was current at the date of registration, or later.
Last updated: 20 - March -2009
Use the tabs at the bottom of the pages to navigate.
© Green Building Council of Australia

## Changelog
Green Star - Office Design v3 & Green Star Office As Built v3
Rating Tool - ChangeLog
Date | Action
2008-02-15 | - Uploaded tool
2008-02-18 | - Removed error message re: update links - Removed reference to Office v3 and added reference to Office Design v3 and Office As Built v3 on all categories - Water Calculator dropdown issue fixed
2008-02-19 | - Sewerage Calculator updated - Water Calculator updated to add clarity and transparency to calculations - Water Benchmarks bug fixed: Calculator used correct Benchmarks, and reported points accurately, but the benchmark table shown to the user did not update properly - Added dropdown to allow user to select appropriate desired type of rating
2008-02-21 | - Updated flow rates for star ratings, form mean value to highest flow rate in each band
2008-03-11 | - Updated the Water Calculator, final version from GHD, with improved error reporting
2008-03-13 | - Included missing N/A clause in Mat -5 Concrete
2008-03-31 | - Fixed first dropdown on potable water calculator
2008-05-13 | - Fixed conditional requirements calculation - Fixed error on sewerage calculator reporting
2008-05-28 | - Fixed Energy calculator reporting for TAS - Fixed Credit Summary page
2008-06-02 | - Minor energy calculator fix
2008-06-13 | - Man-6 'Environmental Managament' credit points box divided into two separate boxes. Does not affect any benchmarks. - Unlocked description boxes, in the blackwater section of the 'Potable Water Calculator' tab - Ammended Sewerage Calculator. Removed calculation which incorrectly included the rainwater into the discharge to sewer calculation. Benchmarks remain unchanged
2008-06-20 | - Unlocked H90-H93 cells in the blackwater section of the 'Potable Water Calculator' tab
2008-08-20 | - Amended Sewerage Calculator to correct improper reporting of points. - Amended Credit Summary Sheet
2008-09-12 | - Amended Credit Summary Sheet to correct improper reporting of credits
2008-11-17 | - Fixed improper reporting in the sewerage calculator on the points awarded to projects that included a rainwater tank. Benchmarks remain unchanged. projects are not penalized for this change - Fixed spelling mistake in sewerage calculator - Added note to the Potable Water Calculator stating that the points in the Tra-3 credit must be filled in. - Added link to the changelog in the frontpage of the tool. Moved the changelog to the front of the tool.
2008-12-17 | - Revised Legionella Credit has been included in the tool
2009-03-17 | - Revised Eco-Conditional Requirement has been included in this tool - New Transport Calculator included in this tool - Added "To be confirmed" totals in the credit summary tab
2009-03-20 | - Amended the transport calculator. The states available are NSW, QLD and VIC

## Introduction
What is Green Star?
What does Green Star - Office Design v3 and Green Star - Office As Built v3 do?
Who can use Green Star - Office Design v3 and Green Star - Office As Built v3?
What do Green Star ratings mean?
Acknowledgements
What is Green Star?
The Green Star environmental rating system for buildings was developed by the Green Building Council of Australia (GBCA). Green Star is Australia’s first comprehensive rating system for evaluating the environmental design and performance of Australian buildings based on a number of criteria, including energy and water efficiency, indoor environment quality and resource conservation.
Green Star has built on existing systems and tools in overseas markets, including the British BREEAM (Building Research Establishment Environmental Assessment Method) system and the North American LEED (Leadership in Energy and Environmental Design) system, by establishing individual environmental measurement criteria relevant to the Australian marketplace and environmental context.
The Green Star rating system was created to:
• define green building by establishing a common language and standard of measurement;
• promote integrated, whole-building design;
• identify building life-cycle impacts;
• raise awareness of green building benefits;
• recognise and reward environmental leadership; and
• transform the built environment to reduce the environmental impact of development.
What does Green Star - Office Design v3 and Green Star - Office As Built v3 do?
Green Star - Office Design v3 and Green Star - Office As Built v3 validates the environmental initiatives of the design phase of new office construction or base building refurbishment; or construction and procurement phase of a Class 5 office building.
The GBCA recommends that you use this rating tool in conjunction with the Green Star - Office Design v3 and Green Star - Office As Built v3 Technical Manual. To obtain a copy, see www.gbcaus.org
Who can use Green Star - Office Design v3 and Green Star - Office As Built v3?
The GBCA encourages all project teams, contractors and other interested parties (e.g. current and/or prospective tenants) to use Green Star - Office Design v3 and Green Star - Office As Built v3 to validate that environmental initiatives of the design phase of new office construction or base building refurbishment; or construction and procurement phase of a Class 5 office building. The use of Green Star - Office Design v3 and Green Star - Office As Built v3 is encouraged on all such projects to assess and improve their environmental design attributes.
The use of Green Star - Office Design v3 and Green Star - Office As Built v3 without formal certification by the GBCA does not entitle the user or any other party to promote the Green Star rating achieved. No fee is payable to the GBCA for such use, however formal recognition of the Green Star rating - and the right to promote same - requires undertaking the formal certification process offered by the GBCA.
All Green Star rating tools are reviewed annually; please forward any feedback to greenstar@gbcaus.org by 30 November each year.
What do Green Star ratings mean?
Green Star rating tools use six stars to measure performance. Projects that obtain a predicted rating of one, two or three stars are not eligible for formal certification. Projects that obtain a predicted 4 Star rating (or above) or above are eligible to apply for formal certification, whereby a:
• 4 Star Green Star Certified Rating recognises and rewards "Best Practice";
• 5 Star Green Star Certified Rating recognises and rewards "Australian Excellence"; and
• 6 Star Green Star Certified Rating recognises and rewards "World Leadership".
The first step in registering a project for formal certification is to contact the GBCA's Technical Manager via e-mail at greenstar@gbcaus.org.
Again, the use of Green Star - Office Design v3 and Green Star - Office As Built v3 without formal certification by the GBCA does not entitle the user or any other party to promote a Green Star rating publicly.
Acknowledgements
The Green Star – Office combines both Green Star – Office Design and Green Star – Office As Built rating tools. The Green Building Council would like to acknowledge all parties that worked on and supported the development of the original Green Star – Office Design and Green Star – Office As Built rating tools.
The GBCA also thanks all those individuals and organisations who provided feedback and expertise to the technical development of the Green Star – Office v3 rating tool and Technical Manual.
The Sustainable Energy Authority of Victoria (SEAV), the Victorian Sustainability Roundtable and the GBCA’s founding members provided much-needed financial support to develop base building Green Star rating tools for the commercial office sector.
Green Star – Office was based on national and international guidelines, including the US LEED Green Building Rating System for Commercial Interiors, the Queensland Government’s Sustainable Development Office Fitout Design Guidelines, Melbourne Docklands ESD Guide, and the Sydney Olympic Park Authority’s Environmental Guidelines 1993. The support of the UK's Building Research Establishment is also acknowledged.

## How to Use
1. | Complete the Building Input worksheet as the building's type and location may affect the predicted rating.
2. | Complete the remaining worksheets by reviewing each credit in each category and entering the number of points you predict the building will achieve in the 'No. of Points Achieved' column. Calculators are provided for a number of the tool's credits.
3. | Enter any points that may be achieved but need to be confirmed in the 'Points to be Confirmed' column.
4. | Enter any comments required in the 'Comments' column.
5. | The predicted rating is shown in the Summary worksheet. More detail on point scores (both achieved and those to be confirmed) are shown in the Credit Summary and Graphical Summary worksheets at the end of the tool.
Limitations
The GBCA does not endorse any self-assessed rating achieved by the use of Green Star - Office. The GBCA offers a formal certification process for ratings of Four Stars and above; this service provides for independent third party review of points claimed to ensure all points can be demonstrated to be achieved by the provision of the necessary documentary evidence. The use of Green Star - Office without formal certification does not entitle the user or any other party to promote the Green Star rating achieved.
The application of Green Star - Office Design v3 & Office As Built v3 to all Class 5 office projects is encouraged to assess and improve their environmental design attributes. No fee is payable to the GBCA for such use, however again formal recognition of the Green Star rating - and the right to promote same - requires undertaking the formal certification process offered by the GBCA.

## Disclaimer
Authorisation, Acknowledgement and Disclaimer
The Green Star environmental rating system for buildings (“Green Star”) and the Green Star – Office rating tool (“Green Star – Office”) have been developed by the Green Building Council of Australia (“GBCA”). Green Star – Office is intended for use by project teams, contractors and other interested parties to validate the environmental initiatives of the design phase of new office construction or base building refurbishment; construction and procurement phase of a Class 5 office building; and/or to validate that environmental initiatives proposed in the design phase have been implemented by the building contractor. As with all Green Star rating tools, Green Star - Office may be subject to further development in the future.
Green Star and Green Star - Office have been developed with the assistance and participation of representatives from many organisations. The views and opinions expressed have been determined upon by the GBCA and its Committees.
Together, Green Star, Green Star - Office and all accompanying documentation represent the GBCA’s approved standard to improve the environmental impact of developments using established and/or advanced industry principles, practices, materials and standards.
The GBCA authorises you to view and use Green Star - Office for your individual use only. In exchange for this authorisation, you agree that the GBCA retains all copyright and other proprietary notices rights contained in and in relation to Green Star - Office and agree not to sell, modify, or use for another purpose the original tool or to reproduce, display or distribute the tool in any way for any public or commercial purpose, including display on a website or in a networked environment. Unauthorised use of Green Star and/or Green Star - Office will violate copyright and other laws, and is prohibited. All text, graphics, layout and other elements of content contained in Green Star and its rating tools are owned by the GBCA and are protected by copyright, trade mark and other laws.
The GBCA does not accept responsibility, including for negligence, for any inaccuracy within Green Star and/or its rating tools and makes no warranty, expressed or implied, including the warranties of merchantability and fitness for a particular purpose, nor assumes any legal liability or responsibility to you or any third parties for the accuracy, completeness, or use of, or reliance on, any information contained in Green Star and/or Green Star – Office, or for any injuries, losses or damages (including, without limitation, equitable relief and economic loss) arising out of such use or reliance.
To the maximum extent permitted by law, the GBCA does not accept responsibility, including without limitation for negligence, for any inaccuracy within Green Star and/or its rating tools and makes no warranty, expressed or implied, including the warranties of merchantability and fitness for a particular purpose, nor assumes any legal liability or responsibility to you or any third parties for the accuracy, completeness, or use of, or reliance on, any information contained in Green Star and/or Green Star – Office, or for any injuries, losses or damages (including, without limitation, equitable relief and economic loss) arising out of such use or reliance.
Green Star and Green Star - Office are no substitute for professional advice. You should seek your own professional and other appropriate advice on the matters addressed by them.
As a condition of use, you covenant not to sue, and agree to waive and release the GBCA, its officers, agents, employees and its members from any and all claims, demands and causes of action for any injury, loss, destruction or damage (including, without limitation, equitable relief and economic loss) that you may now or hereafter have a right to assert against such parties as a result of your use of, or reliance on, Green Star and/or Green Star – Office.
The GBCA does not endorse or otherwise acknowledge the Green Star rating achieved by the use of Green Star – Office. The GBCA offers a formal certification process for ratings of Four Stars and above; this service provides for independent third party review of points claimed to ensure all credits can be demonstrated to be achieved by the provision of the necessary documentary evidence. The use of Green Star - Office without formal certification by the GBCA does not entitle the user or any other party to promote the achieved Green Star rating.
The application of Green Star - Office to all Class 5 commercial office projects is encouraged to assess and improve their environmental attributes. No fee is payable to the GBCA for such use, however again formal recognition of the Green Star rating - and the right to promote same - requires undertaking the formal certification process offered by the GBCA.
You are only authorised to proceed to use Green Star and Green Star – Office on this basis.
All rights reserved.

## Building Input
Green Star - Office Design v3 & Office As Built v3
Building Input WorkSheet
New or Refurbished Building:
Type of Rating
Name of Building:
Address of Building:
Postcode:
State:
Applicant:
Contact Person:
Green Star Accredited Professional:
Project Manager:
Architect:
Structural/Civil Engineer:
Building Services Engineer:
Quantity Surveyor:
Acoustic Consultant:
Landscaping Consultant:
Building Surveyor:
Main Contractor:
Local Planning Authority:
Total Gross Floor Area (GFA) in m2:
Total Class 5 Commercial Office GFA:
% of Commercial Office Space: | 0%
Eligibility for Assessment | Area compliance not met. To be eligible for Green Star assessment, Class 5 Commercial Office GFA must account for at least 80% of the total GFA.
Building Description: (Orientation, Form, Structure, Façade, etc.)
Building Services: (Heating, Cooling, Ventilation, Lighting, Lifts, Domestic Hot Water)
Date:
Current Project Phase:
NB Use of Green Star - Office Design v3 & Office As Built v3 may predict a rating that differs from that achieved via formal Green Star certification. Detailed guidance on credit compliance criteria is contained in the Green Star - Office v3 Manual.
Note on B32: Enter % of gross floor area of development utilised for commercial office purposes.

## Management
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Management
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Man-1 | Green Star Accredited Professional | To encourage and recognise the engagement of professionals who can assist the project team with the integration of Green Star aims and processes throughout design and construction phases. | Two points are awarded where: A principal participant in the design team is a Green Star Accredited Professional and has been engaged by the building owner to provide sustainability advice from the schematic design phase through to construction completion. |  | 2
Man-2 | Commissioning Clauses | To encourage and recognise commissioning and handover initiatives that ensure that all building services can operate to optimal design potential. | Up to two points are awarded as follows: One point is awarded where it is demonstrated that: Comprehensive pre-commissioning, commissioning, and quality monitoring are contractually required to be performed for all building services (BMS, mechanical, electrical and hydraulic); and The works outlined above are done in exact accordance with CIBSE Commissioning Codes or ASHRAE Commissioning Guideline 1-1996 (for mechanical services only). | Ene-1: Energy Commissioning has a significant influence on the actual energy performance of a building. | 1
|  |  | An additional point is awarded where it is demonstrated that: - The point above is achieved; and - The design team and contractor are required to transfer project knowledge to the building owner/manager through all of the following: o Documented design intent; o As-built drawings; o Operations and Maintenance Manual; o Commissioning Report; and o Training of building management staff. |  | 1
Man-3 | Building Tuning | To encourage and recognise commissioning initiatives that ensure optimum occupant comfort and energy efficient services performance throughout the year. | Two points are awarded where: After handover, the building owner implements tuning of all building systems; A relevant member of the design team is involved in the tuning process; Monthly monitoring is undertaken and the outcomes are reported to the building owner quarterly; Full re-commissioning is undertaken 12 months after practical completion; and A Building Tuning Report on the outcomes of the tuning process will be provided to the building owner and made available to the design team. | Ene-1: Energy | 2
Man-4 | Independent Commissioning Agent | To encourage and recognise the appointment of an independent commissioning agent from project design through to handover. | One point is awarded where an independent commissioning agent has been appointed to: Provide commissioning advice to the building owner and the design team; and Monitor and verify the commissioning of all building systems. | Ene-1: Energy | 1
Man-5 | Building Users' Guide | To encourage and recognise information management that enables building users to optimise the building’s environmental performance. | One point is awarded where: A simple and easy-to-use Building Users’ Guide, which includes information relevant for the building users, occupants and tenants’ representatives, is developed and made available to the building owner. |  | 1
Man-6 | Environmental Management | To encourage and recognise the adoption of a formal environmental management system in line with established guidelines during construction. | Up to two points are awarded independently of each other and as follows: One point is awarded where it is demonstrated that: The contractor implements a comprehensive, project-specific Environmental Management Plan (EMP) for the works in accordance with Section 4 of the NSW Environmental Management System guidelines 1998 or 2007. |  | 1
|  |  | One point is awarded where it is demonstrated that:  The Contractor has valid ISO14001 Environmental Management System (EMS) accreditation prior to and throughout the project. |  | 1
Man-7 | Waste Management | To encourage and recognise management practices that minimise the amount of construction waste going to disposal. | Up to two points are awarded where: The contractor implements a Waste Management Plan (WMP), retains waste records and quarterly reports to the building owner; and A percentage (by mass) of all demolition and construction waste is reused or recycled as follows: One point for 60% of the waste; and Two points for 80% of waste. |  | 2
|  |  | Total Points = |  | 12 | 0 | 0
Go to Credit Summary

## IEQ
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Indoor Environment Quality
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
IEQ - 1 | Ventilation Rates | To encourage and recognise designs that provide ample amounts of outside air to counteract build-up of indoor pollutants. | Three points are available as follows: Naturally Ventilated Spaces Three points are awarded where it is demonstrated that 95% of the NLA is naturally ventilated in accordance with AS1668.2-2002. Mechanically Air-conditioned and Mechanically Assisted Naturally Ventilated Spaces Up to three points are awarded where for 95% of the NLA, outside air is provided at rates greater than the requirements of AS1668.2-1991, as follows: One point for 50% improvement; Two points for 100% improvement; and Three points for 150% improvement. Mixed-Mode Ventilated Spaces Both modes of operation must individually satisfy the relevant mechanical and natural ventilation criteria. The points awarded will be limited to the maximum points awarded under the mechanical ventilation criteria. |  | 3
IEQ - 2 | Air Change Effectiveness | To encourage and recognise systems that effectively delivers optimum air quality to any occupant throughout the occupied area. | Two points are awarded where the Air Change Effectiveness (ACE) for at least 95% of the NLA meets the following criteria: Naturally Ventilated Spaces A distribution and laminar flow pattern for at least 90% of each space in the direction of air flow for not less than 95% of standard hours of occupancy is demonstrated. Mechanically Air-conditioned and Mechanically Assisted Naturally Ventilated Spaces The ventilation systems are designed to achieve an Air Change Effectiveness (ACE) of >0.95 for at least 95% of the NLA when measured in accordance with ASHRAE 129-1997: ‘Measuring Air Change Effectiveness’; and ACE is measured in the breathing zone (nominally 1m from finished floor level). Mixed-Mode Ventilated Spaces The ventilation systems are designed to achieve an Air Change Effectiveness (ACE) of >0.95 when measured in accordance with ASHRAE 129-1997: ‘Measuring Air Change Effectiveness’; ACE is measured in the breathing zone (nominally 1m from finished floor level); and A distribution and laminar flow pattern for at least 90% of the NLA of each space in the direction of air flow for 95% of hours of predicted natural ventilation operation is demonstrated. |  | 2
IEQ - 3 | Carbon Dioxide Monitoring and Control | To encourage and recognise the provision of response monitoring of carbon dioxide levels to ensure delivery of optimum quantities of outside air. | One point is awarded where: Naturally ventilated spaces 95% of the NLA is naturally ventilated in accordance with AS1668.2-2002; and Ventilation rates are directly controlled by occupants. Mechanically Air-conditioned and Mechanically Assisted Naturally Ventilated Spaces A carbon dioxide (CO2) monitoring and control system with a minimum of one CO2 sensor at all return points on each floor, is provided to facilitate continuous monitoring and adjustment of outside air ventilation rates to each level, to ensure independent control of ventilation rates to achieve outside air requirements; OR HVAC systems provide 100% outside air with no recirculated component. Mixed-Mode Ventilated Spaces Both modes of operation must satisfy the relevant mechanical and natural ventilation criteria. The points awarded will be limited to the maximum points awarded under the mechanical ventilation criteria. |  | 1
IEQ - 4 | Daylight | To encourage and recognise designs that provides good levels of daylight for building users. | Up to three points are available in his credit; there are two alternative credit criteria: The percentage of the NLA that has a measured Daylight Factor (DF) of not less than 2.0%, at desk-height level (720mm AFFL) under a uniform design sky; OR The percentage of the NLA that has a Daylight Illuminance (DI) of at least 250 Lux. In both cases are the points awarded based on percentage of NLA as per below. One point is awarded for 30% of NLA; Two points are awarded for 60% of NLA; and Three points are awarded for 90% of NLA. |  | 3
IEQ - 5 | Daylight Glare Control | To encourage and recognise buildings that are designed to reduce the discomfort of glare from natural light. | One point is awarded where it is demonstrated that glare from daylight is reduced through any combination of the below: Where, for each typical glazing configuration or atrium, fixed shading devices shade the working plane 1.5m in from the centre of the glazing of direct sun at desk height (720mm AFFL) for 80% of standard working hours; OR Where blinds or screens are fitted on all glazing and atriums as a base building provision and meet to following criteria; - Eliminate all direct sun penetration; - Are control with an automatic monitoring system; - Are equipped with a manual override function accessible by occupants; and - Have a visual light transmittance (VLT) of <10%. |  | 1
IEQ - 6 | High Frequency Ballasts | To encourage and recognise the increase in workplace amenity by avoiding low frequency flicker that may be associated with fluorescent lighting. | One point is awarded where: High frequency ballasts are installed in fluorescent luminaries over a minimum of 95% of the Class 5 Commercial Office NLA. |  | 1
IEQ - 7 | Electric Lighting Levels | To encourage and recognise base building provided office lighting that is not over designed. | One point is awarded where: The office lighting design has a maintained illuminance level of no more than 400 Lux for 95% of the Class 5 Commercial Office NLA as measured at the working plane (720mm AFFL). |  | 1
IEQ - 8 | External Views | To encourage and recognise designs that provide occupants with a visual connection to the external environment. | Up to two points are awarded where: A significant portion of the Class 5 Commercial Office NLA has a direct line of sight to the outdoors or into an adequately sized and day-lit atrium is: - One point for 60% of the NLA; and - Two points for 80% of the NLA. |  | 2
IEQ - 9 | Thermal Comfort | To encourage and recognise buildings that achieve a high level of thermal comfort. | Up to two points are awarded where high level of thermal comfort is achieved for all of the Class 5 Commercial NLA through any combination of the below: Naturally ventilated and mechanically assisted naturally ventilated spaces: Where naturally ventilated buildings achieve credit criteria for IEQ-10 ‘Individual Comfort Control’, up to two points are awarded for if Accessibility Limits of ASHRAE Standard 55-2004 are achieved during Standard Operating Hours of Occupancy for 98% of the year: - One point for internal temperatures within 80% Acceptability Limit 1; and - Two points for internal temperatures within 90% Acceptability Limit 1. Mechanically Air-Conditioned Spaces: Where Predicted Mean Vote (PMV) levels, calculated in accordance with ISO7730, are achieved during Standard Operating Hours of Occupancy for 98% of the year using standard clothing and metabolic rate value: - One point for PMV levels between -1 and +1, inclusive; and - Two points for PMV levels are between -0.5 and +0.5, inclusive. Mixed-mode Ventilated Spaces: For mixed-mode buildings, the above mechanical and natural ventilation thermal comfort criteria must be met. |  | 2
IEQ - 10 | Individual Comfort Control | To encourage and recognise designs that facilitate individual control of thermal comfort. | Up to two points are awarded where it is demonstrated that the base building provides for individual user control of air supply rates, air temperature, or mean radiant temperature to each workspace, through any combination of the below: Naturally Ventilated and Mechanically Assisted Naturally Ventilated Spaces Individual user control over ventilation openings, no less than 0.75m2, is provided as follows: - One point where openings are provided every 30m2 of the NLA; and - Two points where openings are provided every 15m2 of the NLA. Mechanically Air-Conditioned Spaces The base building HVAC system allows for tenant installation of individual user control of thermal comfort to each workspace for each 15m2 or part thereof (including enclosed spaces), as follows: - One point for 60% of NLA; and - Two points for 90% of NLA. Mixed-Mode Ventilated Spaces For mixed-mode buildings, the above mechanical and natural ventilation thermal comfort criteria must be achieved. |  | 2
IEQ - 11 | Hazardous Materials | To encourage and recognise actions taken to reduce health risks to occupants from the presence of hazardous materials. | One point is awarded where: A comprehensive hazardous material survey has been carried out on the project site, as defined by the relevant Environmental and Occupational Health and Safety (OH&S) legislation; and Whenever asbestos, lead or Polychlorinated Biphenyls (PCBs) were found, they have been removed in accordance with the standards listed under Table IEQ-11.1. For new developments or developments in which none of the above hazardous materials were found, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Indoor Environment Quality category score. Type 'na' in the No. of points Achieved column |  | 1
IEQ - 12 | Internal Noise Levels | To encourage and recognise buildings that are designed to maintain internal noise levels at an appropriate level. | Up to two points are awarded where 95% of the project’s NLA does not exceed the ‘Satisfactory’ ambient internal noise levels in accordance with AS/NZS 2107:2000, as follows: Building Services Design - One point is awarded where, within the entire base building general office space, noise from the building services does not exceed 40dBAeq. Overall Building - One point is awarded where within the base building office space, the sound level does not exceed 40dBAeq (assuming open plan offices). |  | 2
IEQ - 13 | Volatile Organic Compounds | To encourage and recognise specification of interior finishes that minimise the contribution and levels of Volatile Organic Compounds in buildings. | Up to three points are awarded where the various finishes used in the project meet the benchmarks outlined below as follows: Paints One point where at least 95% of all painted surfaces meet the TVOC Content Limits outlined in Table IEQ-13.1 (low-VOC) or where no paint is used in the project. |  | 1
|  |  | Carpets and Flooring One point where all carpets meet the TVOC emissions limits outlined in Table IEQ-13.2 (low-VOC); OR Where no carpet has been installed in the project and projects wish to use low-VOC flooring, one point is awarded where all the flooring installed in the project meet the emissions limits outlined in Table IEQ-13.2. Where no carpet has been installed in the project, the carpet point is ‘Not Applicable’ and is removed from the total number of points available for the category; type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
|  |  | Adhesives and Sealants One point where 95% of all adhesives and sealants meet the TVOC Content Limits outlined in Table IEQ-13.3 (low-VOC) or where no adhesives or sealants are used. |  | 1
IEQ - 14 | Formaldehyde Minimisation | To encourage and recognise the specification of products with low formaldehyde emission levels. | One point is awarded where all composite wood products (including exposed and concealed applications) either: Contain low-emission formaldehyde. OR Contain no formaldehyde. If no engineered wood products are used within the project, this credit is ‘Not Applicable’ and is removed from the total number of points available for the category; type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
IEQ - 15 | Mould Prevention | To encourage and recognise the design of services that eliminate the risk of mould growth and its associated detrimental impact on occupant health. | One point is awarded where it is demonstrated that: The mechanically air-conditioned ventilation system actively controls humidity to be no more than 60% relative humidity in the space and no more than 80% relative humidity in the supply ductwork; OR The building is fully naturally ventilated. |  | 1
IEQ - 16 | Tenant Exhaust Riser | To encourage and recognise the design of buildings with a general exhaust riser that can be used by tenants to remove indoor pollutants from printing and photocopy areas. | One point is awarded where the building includes a dedicated tenant’s exhaust riser with the following characteristics: - Complies with section 5.7 of AS1668.2-2002; - Provides no less than 0.2 L/s/m² for 100% of the NLA; - Has a capacity of 0.35 L/s/ m² for 100% of NLA on any individual floor; and - The exhaust system is not recycled to other enclosures of different use. |  | 1
|  |  | Total Points = |  | 27 | 0 | 0
Go to Credit Summary

## Energy
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Energy
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Ene - | Conditional Requirement | To encourage and recognise designs that minimise the greenhouse gas emissions associated with operational energy consumption, and maximise potential operational energy efficiency of the base building. | To meet the conditional requirement: The project’s predicted greenhouse gas emissions must not exceed 110 kgCO2/m2/annum as determined using energy modelling in accordance with: The Australian Building Greenhouse Rating (ABGR) Validation Protocol for Computer Simulations. OR The final and current version of the Green Star Energy Calculator Guide. |  |  | Yes No
Ene - 1 | Greenhouse Gas Emissions | To encourage and recognise designs that minimise greenhouse gas emissions associated with operational energy consumption. | Up to twenty points are awarded where it is demonstrated that the building’s predicted greenhouse gas emissions have been further reduced below the Conditional Requirement. No evidence is required in addition to that submitted for Ene – Conditional Requirement. |  | 20
Ene - 2 | Energy Sub-metering | To encourage and recognise the installation of energy sub-metering to facilitate ongoing management of energy consumption. | Up to two points are awarded as follows: One point is awarded where: It is demonstrated that sub-metering is provided for substantive energy uses within the building (i.e. all energy uses of 100kVa or greater); and There is an effective mechanism for monitoring energy consumption data. |  | 1
|  |  | An additional point is awarded where: - The point above is achieved; - It is demonstrated that sub-metering is provided separately for lighting and separately for power for each floor or tenancy, whichever is smaller; and - There is an effective mechanism for monitoring water consumption data. |  | 1
Ene - 3 | Lighting Power Density | To encourage and recognise designs that provide artificial lighting with minimal energy consumption. | Up to three points are awarded where it is demonstrated that the lighting power densities for 95% of the NLA meets the following criteria at 720mm AFFL with the default maintenance factor of 0.8: One point for energy use of 2.5 W/m² per 100 Lux; Two points for energy use of 2.0 W/m² per 100 Lux; and Three points for energy use of 1.5 W/m² per 100 Lux. |  | 3
Ene - 4 | Lighting Zoning | To encourage and recognise lighting design practices that offer greater flexibility for light switching, making it easier to light only occupied areas. | Up to two points are awarded as follows: One point is awarded where it is demonstrated that: All individual or enclosed spaces are individually switched; The size of individually switched lighting zones does not exceed 100m² for 95% of the NLA; and Switching is clearly labelled and easily accessible by building occupants. |  | 1
|  |  | An additional point is awarded where: - The point above is achieved; and - It is demonstrated that an individually addressable lighting system is provided for 90% of the NLA. |  | 1
Ene - 5 | Peak Energy Demand Reduction | To encourage and recognise designs that reduce peak demand on energy supply infrastructure. | Up to two points are awarded where it is demonstrated that the building has reduced its peak electrical demand load on electricity infrastructure as follows: One point where: Peak electrical demand is actively reduced by 15%; OR The difference between the peak and average demand does not exceed 40%. Two points where: Peak electrical demand is actively reduced by 30%; OR The difference between the peak and average demand does not exceed 20%. |  | 2
|  |  | Total Points = |  | 29 | 0 | 0 |  | 0
Go to Credit Summary

## Ene-1 Calculator
[7 empty] | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Green Star - Office Design v3 & Office As Built v3 | [7 empty] | State/Territory | AGO Full Fuel Cycle Emissions Factor
Green Star Energy Calculator PILOT | [8 empty] | Electricity [kg CO2-e/kWh] | Natural Gas [kg CO2-e/GJ]
[5 empty] | Predicted Greenhouse Gas Emissions (kg CO2-e/m2/annum) | Points Awarded |  |  |  | Small user <100,000 GJ per annum | Large user >100,000 GJ per annum
[8 empty] | NSW / ACT | 1.068 | 71.3 | 68
Note: User must enter values into all white cells | [7 empty] | VIC | 1.325 | 63.6 | 63.4
[5 empty] | 110 | Conditional Req't |  | QLD | 1.046 | 68.8 | 64.2
[5 empty] | 95 | 1 |  | SA | 1.042 | 73.8 | 71.2
Building Location |  |  |  | NSW / ACT | 90 | 2 |  | WA | 0.936 | 60.7 | 60
| MJ/annum | kWh/annum | Greenhouse Gas Coefficient (kg CO2-e/annum) | Resulting Greenhouse Gas Emissions (kg CO2-e/annum) | 85 | 3 |  | TAS | 0.902 | - | -
[5 empty] | 80 | 4 |  | NT | 0.716 | 53.6 | 53.5
[5 empty] | 75 | 5 | [8 empty] | Conditional Req't |  | Ene-1
Total Electricity Consumption |  | 0 | 1.068 | 0 | 70 | 6 |  | Modelling Routes |  |  |  | blank? |  |  | Returned Result
[5 empty] | 65 | 7 |  | Green Star Modelling Route |  |  | 0 | 0 | FALSE |  | TRUE | Yes
Total Gas Consumption | 0 | 0 | 0.25668 | 0 | 60 | 8 | [8 empty] | FALSE | No | 0
[5 empty] | 55 | 9
|  |  | Total Greenhouse Gas Emissions (kg CO2-e/annum) | 0 | 50 | 10
|  |  | Nett Lettable Area (m²) | 0 | 45 | 11
|  |  | Normalised Greenhouse Gas Emissions (kg CO2-e/m²/annum) |  | 40 | 12
[5 empty] | 35 | 13
Ene - Conditional Requirement met? |  |  |  | No | 30 | 14
[5 empty] | 25 | 15
[5 empty] | 20 | 16
[5 empty] | 15 | 17
No. of Ene-1 'Greenhouse Gas Emission' Points Awarded |  |  |  | 0 | 10 | 18
[5 empty] | 5 | 19
[5 empty] | 0 | 20

## Transport
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Transport
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Tra - 1 | Provision of Car Parking | To encourage and recognise developments that facilitate the use of alternative modes of transportation for commuting to work. | Up to two points are awarded as follows: One point is awarded where the number of car parking spaces is: - At least 25% less than the maximum local planning allowances applicable to the project. OR - Not to exceed the minimum planning allowance by more than 10% Two points are awarded where the number of car parking spaces is: - At least 50% less than the maximum local planning allowances applicable to the project. OR - No more than the minimum local planning allowances. Where car parking is not permitted in the local planning scheme, this credit is ‘Not Applicable’ and is excluded from the points available to calculate the Transport Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 2
Tra - 2 | Fuel-Efficient Transport | To encourage and recognise developments that facilitate the use of more fuel efficient vehicles for work commuting. | One point is awarded where: - A minimum of 80% of all preferred parking spaces is dedicated solely for use by car-pool participants, small cars, hybrid or other alternative fuel vehicles; and Of the total parking spaces on the site: - A minimum of 10% or 10 parking spaces (whichever is the greater) are designed and labelled for small vehicles, in accordance with AS/NZS2890.1:2004; and - A minimum of 5% or 5 parking spaces (whichever is the greater) are designed and labelled for mopeds and/or motorbikes, in accordance with AS/NZS2890.1:2004. If no parking spaces are to be provided this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Transport Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Tra - 3 | Cyclist Facilities | To encourage and recognise developments that facilitate the use of bicycles by occupants and visitors. | Up to three points are awarded as follows: One point is awarded where the following are provided: - Secure bicycle storage for 5% of building staff (based on one person per 15m2 of NLA); - Accessible showers (based on one per 10 bicycle spaces provided or part thereof); - Changing facilities adjacent to showers; and - One secure locker per bicycle space in the changing facilities. Two points are awarded where the following are provided: - Secure bicycle storage for 10% of building staff (based on one person per 15m2 of NLA); - Accessible showers (based on one per 10 bicycle spaces provided or part thereof); - Changing facilities adjacent to showers; and - One secure locker per bicycle space in the changing facilities. |  | 2
|  |  | An additional point is awarded where: - The requirements for either one or two points have been met; and - Visitor bicycle parking is provided and meets the following criteria: One space per 750m2 NLA or part thereof; and Provided in an accessible location, signposted and close to, or adjacent to, a major public entrance to the building. |  | 1
Tra - 4 | Commuting Mass Transport | To encourage and recognise developments that facilitate the use of mass transport for work commuting. | Up to five points are awarded for the quality of mass transport options available to building occupants. The points are determined using the Green Star Mass Transport Calculator based on: - The type of mass transport services available within 1000m of the site; - The number of routes served; and - The average interval between services during weekday peak hours. The points are determined using the Green Star Public Transport Calculator. |  | 5 | 0
[5 empty] | 11 | 0 | 0
Go to Credit Summary
Go to Transport Calculator

## Public Transport Calculator
[7 empty] | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Green Star - Office Design v3 & Office As Built v3 |  |  |  |  | Points Achieved | 0
Credit Summary for: | [7 empty] | Transport Engine (HIDDEN)
Public Transport Calculator | [7 empty] | The weighting factors and score matrix to be calibrated using assessments of different office locations
| Deemed to satisfy |  |  |  | HOW TO USE THE TRANSPORT CALCULATOR Deemed to Satisfy Criteria If eligible, select the postcode in the Deemed to Satisfy Criteria. No other details are required. Bus, Tram and/or Ferry Determine number of Bus, Tram or Ferry Services options within 1km of the building and the walking distance to each, and follow the instructions in the Transport Calculator Guide. Train There are two input options for Trains: - For “No. of Train Services”, determine number of Train Services options within 1km of the building and the walking distance to each, and follow the instructions in the Transport Calculator Guide. - For “Train Stations”, select a State (Only available in NSW, QLD and VIC), Train Station, and Distance from the drop down list’s. Note: Up to four Train Stations within 1km of the building can be entered.
Deemed to satisfy points
| Please see the Transport - Deemed to Satisfy Criteria for more information at: http://www.gbca.org.au/green-star/technical-clarifications-cir-rulings/transport-deemed-to-satisfy-criteria/1699.htm | [8 empty] | Points/credits
| Postcode | [8 empty] | 0
| Select Postcode | Select Postcode
OR
| Bus, Tram and/or Ferry | [7 empty] | Manual input | [7 empty] | Score Matrix |  |  |  | Deemed to satisfy postcodes |  |  |  |  | Points achieved for selected train station = NB:When more stations are added - this formula needs editing |  |  |  |  | 0 |  | Table used to work out score matrix points |  |  | Points achieved for selected train station(s)
| No. of Bus, Tram or Ferry Services | [19 empty] | Select Postcode | Points |  | Train Stations |  | This corresponds to this many points in the score matrix = |  |  |  |  | 0 |  | Credits | No. of points Achieved |  | 0 | Train Station (Row 1)
| Walking Distance from Building Entrance to Public Transport | Frequency of Service during Peak Periods | [6 empty] | Tram, Bus & Ferry | Weighting factors |  | Score Achieved |  |  |  |  | No. of points Achieved | Credits |  |  | NSW 2000 | 5 |  |  |  | Concatenated name for Vlookup | Row index for HLOOKUP. | Walking Distance from Building Entrance to Public Transport |  |  |  |  | 0 | 0 |  | 0 | Train Station (Row 2)
|  | 15 min | 30 min | [6 empty] | 15min | 30min | [5 empty] | 10 | 1 |  |  | NSW 2010 | 5 |  | Select State | Select Train Station |  | 1 | 0-250m | 250-500m | 500-750m | 750m-1km |  | 1 | 10 |  | 0 | Train Station (Row 3)
| 0-250m | [8 empty] | 6 | 4 | 0 |  |  |  |  | 20 | 2 |  |  | NSW 2060 | 5 |  | NSW | Blacktown | NSWBlacktown | 2 | 1 | 1 | 1 | 0 |  | 2 | 20 |  | 0 | Train Station (Row 4)
| 250-500m | [8 empty] | 5 | 3 | 0 |  |  |  |  | 40 | 3 |  |  | QLD 4000 | 5 |  | NSW | Burwood | NSWBurwood | 3 | 2 | 2 | 2 | 1 |  | 3 | 40 |  | 0
| 500-750m | [8 empty] | 4 | 2 | 0 |  |  |  |  | 60 | 4 |  |  | SA 5000 | 5 |  | NSW | Cabramatta | NSWCabramatta | 4 | 1 | 1 | 1 | 1 |  | 4 | 60
| 750m-1km | [8 empty] | 3 | 1 | 0 |  |  |  |  | 80 | 5 |  |  | VIC 3000 | 5 |  | NSW | Campbelltown | NSWCampbelltown | 5 | 1 | 1 | 1 | 0 |  | 5 | 80
[11 empty] | Subtotal for tram, buses and ferry | 0 | [8 empty] | VIC 3008 | 5 |  | NSW | Epping | NSWEpping | 6 | 1 | 1 | 1 | 0
| Train | [19 empty] | VIC 3121 | 5 |  | NSW | Glenfield | NSWGlenfield | 7 | 2 | 2 | 2 | 1
| Add points from Trains by entering: |  |  | Select Train input option | [16 empty] | VIC 3205 | 5 |  | NSW | Lidcombe | NSWLidcombe | 8 | 3 | 3 | 2 | 2
| No. of Train Services |  |  | Train Station (Only available in 'NSW' 'QLD' 'VIC') | [19 empty] | NSW | Liverpool | NSWLiverpool | 9 | 1 | 1 | 1 | 0
| Walking Distance from Building Entrance to Public Transport | Frequency of Service during Peak Periods |  | State | Train Station | Walking Distance from Building Entrance to Public Transport |  |  | Train | Weighting factors |  | No. of Train Services | Train Station |  |  |  | Final Points= | 0 | [5 empty] | NSW | Milsons Point | NSWMilsons Point | 10 | 2 | 2 | 1 | 1
|  | 15 min | 30 min | [6 empty] | 7 | 5 | 0 | [11 empty] | NSW | Parramatta | NSWParramatta | 11 | 1 | 1 | 1 | 0
| 0-250m |  |  | NSW | Select Train Station | Select Distance |  |  |  | 6 | 4 | 0 | [11 empty] | NSW | Redfern | NSWRedfern | 12 | 4 | 4 | 3 | 3
| 250-500m |  |  |  | Select Train Station | Select Distance |  |  |  | 5 | 3 | 0 | [11 empty] | NSW | Strathfield | NSWStrathfield | 13 | 3 | 2 | 2 | 2
| 500-750m |  |  |  | Select Train Station | Select Distance |  |  |  | 4 | 2 | 0 | [11 empty] | NSW | Sydenham | NSWSydenham | 14 | 2 | 2 | 2 | 1
| 750m-1km |  |  |  | Select Train Station | Select Distance |  |  |  |  | Subtotal for trains | 0 | 0 | [10 empty] | NSW | Westmead | NSWWestmead | 15 | 1 | 1 | 1 | 0
[10 empty] | TOTAL SCORE CALCULATED FROM MANUAL ENTRY= |  | 0 | [11 empty] | NSW | Wolli Creek | NSWWolli Creek | 16 | 2 | 2 | 2 | 1
[24 empty] | VIC | Camberwell | VICCamberwell | 17 | 2 | 2 | 2 | 1
[24 empty] | VIC | Caulfield | VICCaulfield | 18 | 2 | 2 | 2 | 2
[24 empty] | VIC | Clifton Hill | VICClifton Hill | 19 | 2 | 2 | 2 | 1
[24 empty] | VIC | Footscray | VICFootscray | 20 | 2 | 2 | 2 | 1
[24 empty] | VIC | Jolimont | VICJolimont | 21 | 2 | 2 | 2 | 1
[24 empty] | VIC | North Melbourne | VICNorth Melbourne | 22 | 3 | 3 | 2 | 2
[24 empty] | VIC | South Yarra | VICSouth Yarra | 23 | 3 | 3 | 2 | 2
[24 empty] | QLD | Albion | QLDAlbion | 24 | 2 | 1 | 1 | 0
[24 empty] | QLD | Bowen Hills | QLDBowen Hills | 25 | 4 | 3 | 3 | 2
[24 empty] | QLD | Eagle Junction | QLDEagle Junction | 26 | 2 | 2 | 1 | 1
[24 empty] | QLD | Fortitude Valley (Brunswick Street) | QLDFortitude Valley (Brunswick Street) | 27 | 4 | 3 | 3 | 2
[24 empty] | QLD | Northgate | QLDNorthgate | 28 | 2 | 1 | 1 | 0
[24 empty] | QLD | Nundah | QLDNundah | 29 | 1 | 1 | 0 | 0
[24 empty] | QLD | Park Road | QLDPark Road | 30 | 2 | 1 | 1 | 0
[24 empty] | QLD | South Bank | QLDSouth Bank | 31 | 2 | 2 | 1 | 1
[24 empty] | QLD | South Brisbane | QLDSouth Brisbane | 32 | 2 | 2 | 1 | 1
[24 empty] | QLD | Toombul | QLDToombul | 33 | 1 | 1 | 0 | 0
[24 empty] | QLD | Wooloomin | QLDWooloomin | 34 | 2 | 1 | 1 | 0
Back to Transport Credits

## Water
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Water
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Wat - 1 | Occupant Amenity Water | To encourage and recognise designs that reduce potable water consumption by building occupants. | Up to five points are awarded where the predicted potable water consumption for sanitary use within the building has been reduced against a ‘best practice’ benchmark. The points are determined by the Green Star Potable Water Calculator. |  | 5 | 0
Wat - 2 | Water Meters | To encourage and recognise the design of systems that both monitor and manage water consumption. | One point is awarded where: - Water meters are installed for all major water uses in the project; and - There is an effective mechanism for monitoring water consumption data. |  | 1
Wat - 3 | Landscape Irrigation | To encourage and recognise the design of systems that aim to reduce the consumption of potable water for landscape irrigation | One point is awarded where: - Potable water consumption for landscape irrigation has been reduced by 90% OR - A xeriscape garden has been installed. If there is no landscaping, or landscaping represents less than 1% of the site area, this point is ‘Not Applicable’ and is excluded from the points available used to calculate the Water Category Score. Type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Wat - 4 | Heat Rejection Water | To encourage and recognise design that reduces potable water consumption from heat rejection systems. | Up to four points are awarded as follows: Two points are awarded where: - Potable water consumption of water-based heat rejection systems is reduced by 50%; and Four points are awarded where: - Potable water consumption of water-based heat rejection systems is reduced by 90%; OR - No water-based heat rejection systems are provided. |  | 4
Wat - 5 | Fire System Water Consumption | To encourage and recognise building design which reduces consumption of potable water for the building's fire protection and essential water storage systems. | One point is awarded where: - There is sufficient temporary storage for a minimum of 80% of the routine fire protection system test water and maintenance drain-downs, for reuse on-site; and - Each floor fitted with a sprinkler system has isolation valves or shut-off points for floor-by-floor testing; OR - The fire protection system does not expel water for testing. If the building does not have a sprinkler system, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Water Category Score. Type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
|  |  | Total Points = |  | 12 | 0 | 0
Go to Credit Summary
Go to Water Calculator

## Potable Water Calculator
[10 empty] | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Green Star - Office Design v3 & Office As Built v3
Credit Summary for: |  | 0 | [7 empty] | ALL THESE COLUMNS ARE HIDDEN
Potable Water Calculator |  |  |  | Points Achieved |  |  | 0 |  |  | Selections | Factors | Calculation | Unit or description
|  |  |  | Gross Floor Area (m2) |  |  | 0 |  |  | 1 | Hours of operation | 1 | Potable water factor
[12 empty] | 0 | Assumed number of occupants
Please ensure that points in the Tra-3 credit have been filled in prior to using this calculator.
PREDICTED POTABLE WATER CONSUMPTION
| WCs |  | Star Rating | Avg L/flush |  | % of WCs |  |  |  | Star rating
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
[6 empty] | 0% |  | No WCs |  |  |  | 0 | Number of toilet flushes per day for occupancy
| Predicted WC Water Consumption from calculation L/day/m2 |  |  |  |  | 0 |  | Error |  |  |  | 0 | Total L/day for WC
| Urinal Flush Controls |  | Star Rating | Avg L/flush |  | % of urinals |  |  |  | Star rating |  |  |  | Autoflush L/day (if selected)
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit | 0
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit | 0
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit | 0
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit | 0
| Total % Urinal Flush Controls |  |  |  |  | 0% | [5 empty] | 0 | Total L/day for Urinals
| Urinals on Auto Flush |  | Number of Cisterns | Avg L/flush |  | % of Floor Area Served | [5 empty] | 0 | Number of urinal flushes per day for occupancy
|  |  | 0 | 0 |  | 0% | [5 empty] | 0 | Total L/day for autoflush Urinals | 0
| Total % Urinals |  |  |  |  | 0% |  | No Urinals
| Predicted Urinal Water Consumption from calculation L/day/m2 |  |  |  |  | 0 |  | Error |  | No Urinals
[12 empty] | 0 | Total L/day for all Urinals
| Indoor Taps |  | Star Rating | Avg L/min |  | % of taps
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
[6 empty] | 0% |  | No Indoor Taps |  |  |  | 0 | Total Occupancy tap duration
| Predicted Indoor tap Water Consumption from calculation L/day/m2 |  |  |  |  | 0 |  | Error |  |  |  | 0 | Total L/day for Indoor taps
| Showerheads |  |  | L/minute |  | % of showers
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
| <enter description here> |  |  | 0 |  | 0% |  |  |  | 1 |  | 0 | L/day for this unit
[6 empty] | 0% |  | No Showerheads |  |  |  | 0 | Total occupancy shower duration
| Predicted Showerhead Water Consumption from calculation L/day/m2 |  |  |  |  | 0 |  | Error |  |  |  | 0 | Total L/day for Showers
The following estimated total potable water consumption is based on the data entered above. The water consumption of the fittings per m2 is based on assumptions of typical office usage and does not represent actual water consumption in the building.
| Predicted Water Consumption from calculation |  |  |  |  | 0 |  | L/day/m2 |  |  |  | 0 | Total from all fittings above
| WCs |  |  |  |  | 0 |  | L/day/m2 | Error
| Urinals |  |  |  |  | 0 |  | L/day/m2
| Indoor Taps |  |  |  |  | 0 |  | L/day/m2 | Error
| Showersheads |  |  |  |  | 0 |  | L/day/m2
OTHER PREDICTED RECYCLED WATER CONSUMPTION
| Are there any other recycled water demands in the project? Enter recycled water demand only, disregard potable water use. Reductions in potable water use are awarded in other Water credits in the Green Star tool. | [8 empty] | 1 |  |  |  |  | Logic | Total | Total if true
| RECYCLED WATER DEMAND FOR IRRIGATION (L/day) |  |  |  |  | 0 |  |  |  | 0
| RECYCLED WATER DEMAND FOR COOLING TOWERS (L/day) |  |  |  |  | 0 |  |  |  | 0
| RECYCLED WATER DEMAND FOR FIRE SYSTEM TESTING (L/day) |  |  |  |  | 0 |  |  |  | 0 |  | 0 | All predicted recycled water consumption
[12 empty] | #DIV/0! | L/day/m2
PREDICTED REDUCTION IN POTABLE WATER CONSUMPTION
| RAINWATER HARVESTING | [15 empty] | 0
| Are there any rainwater harvesting systems, and if so, do they comply with Local Authority requirements? | [8 empty] | 1
| Rainwater collected is used for (please tick appropriate box(es)): | [12 empty] | RAINWATER TANK BALANCE CALCULATIONS
|  | Irrigation |  | WC & Urinal Flushing | [5 empty] | FALSE | FALSE | 0 | 0
|  | Cooling Tower |  | Shower & Taps (treated to potable) | [5 empty] | FALSE | FALSE | 0 | 0
|  | Fire System Testing |  | Other (daily demand in kL) |  |  | 0 |  |  | FALSE | FALSE | 0 | 0 | 0 | sum of all recycled water demand
| Rainfall collection area to storage tank (m2) | [12 empty] | Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Annual Totals | kL/m2/day
| Storage capacity of rainwater tank (kL) | [12 empty] | Avg monthly rainfall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rainwater Run-off Coefficient | [5 empty] | 0 |  |  |  |  | 0 | Rainwater demand kL/day | Monthly yield | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0!
| Average monthly rainfall for the building location (mm) Link to Bureau of Meterology: http://www.bom.gov.au/climate/averages/ | [8 empty] | 1 |  | 0 | Roof area into tank m2 | Monthly demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0!
| To obtain the rainfall data and number of rain days for your region, go to the link above and choose your area. Then copy data to all fields. | Jan. | Feb. | March | April | May | June |  |  |  |  | 0 | Storage capacity kL | Overflow to drain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0!
[12 empty] | 0 | Runoff coefficient | Volume at month end | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | July | August | Sept. | Oct. | Nov. | Dec. |  |  |  |  | 0 | month no of raindays | Top up water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0!
|  | Annual number of rain days >1mm: | [11 empty] | Monthly effective use | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0!
| Predicted potable water reduction due to rainwater harvesting (L/day/m2) |  |  |  |  | 0 | [5 empty] | 0 | kL/day harvested for selected demand | days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 |  | 365
[14 empty] | 0 Month: Tank Efficiency |  | #DIV/0!
GREYWATER HARVESTING
| Are there any greywater harvesting systems, and if so, do they comply with Local Authority requirements? | [8 empty] | 1
Greywater harvested is used for (please tick appropriate box(es)):
|  | Irrigation |  | WC & Urinal Flushing | [5 empty] | FALSE | FALSE | 0 | 0
|  | Cooling Tower |  | Shower & Taps (treated to potable) | [5 empty] | FALSE | FALSE | 0 | 0
|  | Fire System Testing |  | Other (daily demand in kL) |  |  | 0 |  |  | FALSE | FALSE | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: sum of all recycled water demand
| Percentage of indoor taps used for greywater collection | [10 empty] | 0 | L/day from taps
| Percentage of showers used for greywater collection | [10 empty] | 0 | L/day from showers
Storage capacity of Greywater tank (kL)
| Other greywater Collection Sources |  |  |  |  | L/day
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | L/day from all other sources
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | Total L/day harvested
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | Daily demand for selected use
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | L/day harvested for selected demand
| Predicted potable water replacement due to greywater harvesting (L/day/m2): |  |  |  |  | 0
0
BLACKWATER HARVESTING
| Are there any blackwater harvesting systems, and if so, do they comply with Local Authority requirements? | [8 empty] | 1
Blackwater harvested is used for (please tick appropriate box(es)):
|  | Irrigation |  | WC & Urinal Flushing | [5 empty] | FALSE | FALSE | 0 | 0
|  | Cooling Tower |  | Shower & Taps (treated to potable) | [5 empty] | FALSE | FALSE | 0 | 0
|  | Fire System Testing |  | Other (daily demand in kL) |  |  | 3 |  |  | FALSE | FALSE | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: sum of all recycled water demand
| Percentage of WC's used for blackwater collection |  |  |  |  | 0% | [5 empty] | 0
| Percentage of urinals used for blackwater collection |  |  |  |  | 0% | [5 empty] | 0
| Percentage of indoor taps used for blackwater collection |  |  |  |  | 0% | [5 empty] | 0
| Percentage of showers used for blackwater collection |  |  |  |  | 0% | [5 empty] | 0
| Storage capacity of Blackwater tank (kL) |  |  |  |  | 0
| Other blackwater collection sources |  |  |  |  | L/day
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | L/day from all other sources
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | Total L/day harvested
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | Daily demand for selected use
| <enter description here> |  |  |  |  | 0 | [5 empty] | 0 | L/day harvested for selected demand
| Predicted potable water replacement due to blackwater harvesting (L/day/m2): |  |  |  |  | 0
The following estimated total reductions in potable water consumption is based on the data entered above and does not represent actual reduction of water consumption in the building.
| Total Predicted Reduction in Potable Water Consumption |  |  |  |  | 0 |  | L/day/m2
| Rainwater |  |  |  |  | 0 |  | L/day/m2
| Greywater |  |  |  |  | 0 |  | L/day/m2
| Blackwater |  |  |  |  | 0 |  | L/day/m2
PREDICTED RECYCLED WATER AVAILABLE TO FIXTURES
The following estimated total predicted availability of water to fixtures is based on the data entered above and does not represent actual available water for consumption by fixtures within the building.
| Predicted Reduction in Potable Water Consumption |  |  |  |  | 0 |  | L/day/m2
| Other Predicted Recycled Water Consumption |  |  |  |  | 0 |  | L/day/m2
| Total Predicted Recycled Water available to Fixtures |  |  |  |  | 0 |  | L/day/m2
TOTAL REDUCED POTABLE WATER USE
| Predicted Potable Water Consumption from Fixtures |  |  |  |  | 0 |  | L/day/m2 |  | 0
| Predicted Recycled Water available to Fixtures |  |  |  |  | 0 |  | L/day/m2
| NET POTABLE WATER CONSUMPTION |  |  |  |  | 0 |  | L/day/m2
| POINTS ACHIEVED: |  |  |  |  | 0
Tables used for calculation and selection | bar: 0 Month to sum of all recycled water demand Apr
WELS Fixture Flow Rates (Averaged where a range is permitted)
| Wat-1 Occupant Amenity Water Predicted Potable Water Rating Benchmark | [8 empty] | no | Fittings selection | WC Avg l/flush | Urinal Avg l/flush one urinal | 0 Month: Taps Avg L/min; sum of all recycled water demand Jan: Showerheads Avg L/min; sum of all recycled water demand Feb: Urinal Avg l/flush in group of 2
| L/day/m2 |  |  | Points achieved | [5 empty] | 1 |  |  | 0
| 0.19 |  |  | 5 | [5 empty] | 2 | 0 Star | Warning | 2.5 | 0 Month: Warning; sum of all recycled water demand Jan: 16; sum of all recycled water demand Feb: 4
| 0.28 |  |  | 4 | [5 empty] | 3 | 1 Star | 5.5 | 2.5 | 0 Month: 16; sum of all recycled water demand Jan: 16; sum of all recycled water demand Feb: 4
| 0.37 |  |  | 3 | [5 empty] | 4 | 2 Star | 4.5 | 2.5 | 0 Month: 12; sum of all recycled water demand Jan: 12; sum of all recycled water demand Feb: 2.5
| 0.47 |  |  | 2 | [5 empty] | 5 | 3 Star | 4 | 2 | 0 Month: 9; sum of all recycled water demand Jan: 9; sum of all recycled water demand Feb: 2
| 0.57 |  |  | 1 | [5 empty] | 6 | 4 Star | 3.5 | 1.5 | 0 Month: 7.5; sum of all recycled water demand Jan: 9; sum of all recycled water demand Feb: 1.5
[10 empty] | 7 | 5 Star | 3 | 1 | 0 Month: 6; sum of all recycled water demand Jan: 9; sum of all recycled water demand Feb: 1
[10 empty] | 8 | 6 Star | 2.5 | 1 | 0 Month: 4.5; sum of all recycled water demand Jan: 9; sum of all recycled water demand Feb: 0.75
[10 empty] | 9 | Unknown | To be entered | To be entered | 0 Month: To be entered; sum of all recycled water demand Jan: To be entered; sum of all recycled water demand Feb: To be entered
[10 empty] | 10 | Waterless | N/A | 0 | 0 Month: N/A; sum of all recycled water demand Jan: N/A; sum of all recycled water demand Feb: N/A
Rainfall Runoff Co-efficients | bar: 0 Month to sum of all recycled water demand Aug; sum of all recycled water demand Oct
1 | bar: sum of all recycled water demand Jan to sum of all recycled water demand Aug; sum of all recycled water demand Oct
[10 empty] | 2 | Pitched tile roof (> 30 pitch) |  | 0.9 | bar: sum of all recycled water demand Jan to sum of all recycled water demand Aug; sum of all recycled water demand Oct
[10 empty] | 3 | Steel roof (> 30 pitch) |  | 0.8 | bar: sum of all recycled water demand Jan to sum of all recycled water demand Aug; sum of all recycled water demand Oct
[10 empty] | 4 | Flat smooth roof (30 Pitch) |  | 0.5 | bar: sum of all recycled water demand Jan to sum of all recycled water demand Aug
[10 empty] | 5 | Flat gravel or turf roof (<30 pitch) |  | 0.4 | bar: sum of all recycled water demand Jan
Decision
[10 empty] | 1 | No
[10 empty] | 2 | Yes
[10 empty] | Collected water use |  |  |  | 0 Month: Daily demand (kL)
[10 empty] | 1 | Irrigation |  |  | 0 Month: 0
[10 empty] | 2 | Cooling Tower |  |  | 0 Month: 0
[10 empty] | 3 | Fire System Testing |  |  | 0 Month: 0
[10 empty] | 4 | WC& Urinals |  |  | 0 Month: 0; sum of all recycled water demand Jan: 0
[10 empty] | 5 | Taps& Showers |  |  | 0 Month: 0
[10 empty] | 6 | Other |  |  | 0 Month: 0
Hours of operation potable water factor (selected from buidling input screen)
[10 empty] | 1 | Standard | 1
[10 empty] | 2 | 7 days a week | 1.4
[10 empty] | 3 | 24 hours / 5 days | 2
[10 empty] | 4 | 24 hours / 7 days | 2.8
[10 empty] | # of Tra-3 points | L/day/m2 benchmark (based on all fittings of same water rating) |  |  | 0 Month: Credits
[10 empty] | 0 | No showers installed | Showers for 5% of staff - (see Tra-3) | Showers for 10% of staff - (See Tra-3) | bar: 0 Month
[11 empty] | 0 | 1 | 2 | bar: 0 Month
[11 empty] | 0.19 | 0.27 | 0.31 | 0 Month: 5
[11 empty] | 0.28 | 0.4 | 0.46 | 0 Month: 4
[11 empty] | 0.37 | 0.53 | 0.64 | 0 Month: 3
[11 empty] | 0.47 | 0.67 | 0.77 | 0 Month: 2
[11 empty] | 0.57 | 0.8 | 0.93 | bar: 0 Month
Parameters
[10 empty] | Name | Value | Description
General
[10 empty] | WC uses male | 0.3 | Average per person (50% of occupation) | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | WC uses female | 2.3 | Average per person (50% of occupation) | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Urinal uses | 2 | Average per person (50% of occupation) | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | No urinals installed | 2.3 | WC uses per day per person. | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Urinal auto timer | 48 | times flushing per day based on flushing every 30 minutes | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | handwashing duration | 0.15 | minutes | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Duration of showers | 5 | minutes per person per business day. Is this still needed as the shower demand has been removed...??? | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Shower use | 5% | of all occupants | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Female Occupancy | 50% | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Male Occupancy | 50% | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Tap usage | 2.5 | per day for male and female | bar: 0 Month to sum of all recycled water demand Apr
Rainwater tank | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Rainwater tank first flush volume | 20 | litres per 100m2 | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | Harvesting\ for | Irrigation | Cooling Tower | Fire Systems Testing | 0 Month: WC and Urinals; sum of all recycled water demand Jan: Showers and taps; sum of all recycled water demand Feb: Other
[10 empty] | Rainwater | 0 | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: 0; sum of all recycled water demand Feb: 0
[10 empty] | Greywater | 0 | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: 0; sum of all recycled water demand Feb: 0
[10 empty] | Blackwater | 0 | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: 0; sum of all recycled water demand Feb: 0
[10 empty] | Total | 0 | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: 0; sum of all recycled water demand Feb: 0
[10 empty] | Max consumable | 0 | 0 | 0 | 0 Month: 0; sum of all recycled water demand Jan: 0
[10 empty] | Split demand | 1 | 1 | 1 | bar: 0 Month to sum of all recycled water demand Apr
[10 empty] | % sewer reduction | L/day/m2 benchmark ((L/day/person)/(m2/person)) |  |  | 0 Month: Credits; sum of all recycled water demand Jan: Calc (0%); sum of all recycled water demand Feb: Calc (10%); sum of all recycled water demand Mar: Calc (15%)
[11 empty] | No showers installed | Medium Demand (10%) | High Demand (15%) | bar: 0 Month to sum of all recycled water demand Mar
[10 empty] | 90% | 0.1 | 0.14 | 0.16 | 0 Month: 4; sum of all recycled water demand Jan: 1; sum of all recycled water demand Feb: 1; sum of all recycled water demand Mar: 1
[10 empty] | 70% | 0.3 | 0.42 | 0.48 | 0 Month: 3; sum of all recycled water demand Jan: 1; sum of all recycled water demand Feb: 1; sum of all recycled water demand Mar: 1
[10 empty] | 50% | 0.5 | 0.7 | 0.8 | 0 Month: 2; sum of all recycled water demand Jan: 1; sum of all recycled water demand Feb: 1; sum of all recycled water demand Mar: 1
[10 empty] | 40% | 0.6 | 0.84 | 0.96 | bar: 0 Month to sum of all recycled water demand Mar
[10 empty] | 0% | 1 | 1.4 | 1.6 | bar: 0 Month to sum of all recycled water demand Mar
[15 empty] | 4 | 4 | 4
Note on C58: Enter irrigation demand even if not fed by the potable water supply
Note on C59: Enter demand even if not fed by the potable water supply
Note on C60: Enter demand even if not fed by the potable water supply
Note on C92: For fire services and condensate or other flows, first calculate the annual collection and convert to daily rates
Note on C93: For fire services and condensate or other flows, first calculate the annual collection and convert to daily rates
Note on C94: For fire services and condensate or other flows, first calculate the annual collection and convert to daily rates
Note on C95: For fire services and condensate or other flows, first calculate the annual collection and convert to daily rates
Note on E11: Refer Manual for Water Efficiency Labelling. Optional for selection to populate usage. Assume 1A rating for any fixtures where the water consumption is not known. OPTIONAL NOTE: If the value populated is overwritten, any consecutive selection of the star rating will not populate the value anymore!.
Note on F6: From Buidling Input Sheet
Note on F11: This number is generated when selecting a star rating, but can be overwritten by the user. Once overwritten, any consecutive star rating selection will NOT populate the average value.
Note on F19: This number is generated when selecting a star rating, but can be overwritten by the user. Once overwritten, any consecutive star rating selection will NOT populate the average value.
Note on F30: This number is generated when selecting a star rating, but can be overwritten by the user. Once overwritten, any consecutive star rating selection will NOT populate the average value.
Note on F38: This number is generated when selecting a star rating, but can be overwritten by the user. Once overwritten, any consecutive star rating selection will NOT populate the average value.
Note on M6: From building input sheet
Note on N68: elindner: Irrigation
Note on N85: elindner: Irrigation
Note on N102: elindner: Irrigation
Note on N143: Need to define this, as the tool will need to use a figure to calculate the data
Note on N150: : Assume 1 star?
Note on N151: : Assume 1 star?
Note on N152: : Assume 1 star?
Note on O143: Need to evaluate this figure according to the WELS table
Note on O149: Need to evaluate this figure according to the WELS table
Note on P72: Andrew: Melbourne used
Note on P74: Andrew: These values are conditional and their origin is dependant on rainwater, grey water, and blackwater options 1 to 5
Note on P93: Andrew: These values are conditional and their origin is dependant on rainwater, grey water, and blackwater options 1 to 5
Note on P143: Need to define this, as the tool will need to use a figure to calculate the data
Note on Q73: elindner: Rain collection on rain days - first flush
Note on R143: Need to evaluate this figure according to the WELS table
Note on R144: Need to evaluate this figure according to the WELS table
Note on R149: Need to evaluate this figure according to the WELS table
Back to Water Credits

## Materials
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Materials
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Mat - 1 | Recycling Waste Storage | To encourage and recognise the inclusion of storage space that facilitates the recycling of resources used within buildings to reduce waste going to landfill. | Two points are awarded where a dedicated storage area for the separation and collection of office recyclables is provided and it: - Is adequately sized in accordance with ‘Sizing the Waste Storage Area’ table (Table Mat-1.1); - Meets the access requirements of 'Policy for Waste Minimisation in New Developments' (NSW, 2004): Section A, points A-12 through A-17, and Section C, points C6 and C7; and - Is located in the same level as the loading dock with clearly marked, sign-posted, convenient, guaranteed access route within one of the following walking distances: - 20m of the exit used for recycling pick-up; OR - 20m of the lift core serving all floors; OR - 3m of the shortest route connecting the lift core serving all floors and the exit used for recycling pick-up. |  | 2
Mat - 2 | Building Reuse | To encourage and recognise developments that reuse existing buildings to minimise materials consumption. | Six points are available as follows: Up to two points are awarded where a proportion of the total existing façade of the building, by vertical area, is reused: - One point for reuse of 60%; or - Two points for reuse of 90%. Up to four points are awarded where a proportion of the existing major structure, by gross building volume, is reused: - Two points for 30% reuse; - Three points for 60% reuse; or - Four points for 90%. Where the site contained no buildings at the time of purchase or the total GFA of the original building(s) is less than 20% of the GFA of the new building that replaces it, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 6
Mat - 3 | Reused Materials | To encourage and recognise designs that prolong the useful life of existing products and materials. | One point is awarded where: At least 2% of the project’s total contract value is represented by reused products/materials. This credit excludes materials specifically addressed by other credits (i.e. steel, concrete, PVC and timber); neither does it address the reuse of the original building(s) on the site (addressed in Mat-2 ‘Building Reuse’). |  | 1
Mat - 4 | Shell and Core or Integrated Fit-out | To encourage and recognise base building delivery mechanisms that eliminate the need for immediate tenant refits. | Two points are available as follows: Up to two points are awarded where a percentage of the (NLA) of the project is delivered as any combination of shell and core or integrated fitout. - One point for 60% of NLA; or - Two points for 90% of NLA. |  | 2
Mat - 5 | Concrete | To encourage and recognise the reduction of embodied energy and resource depletion occurring through use of concrete. | Three points are available as follows: Up to three points are available where the project has reduced the absolute quantity of Portland cement, as an average across all concrete mixes, by substituting it with industrial waste product(s) or oversized aggregate as follows: - For 1 point, 30% for in-situ concrete, 20% for pre-cast concrete and 15% for stressed concrete; or - For 2 points, 60% for in-situ concrete, 40% for pre-cast concrete and 30% for stressed concrete. |  | 2
|  |  | An additional point is awarded where: - At least one of the above points is achieved; - 20% of all aggregate used for structural purposes is recycled (Class 1 RCA in accordance with HB155-2002) or slag aggregate; and - No natural aggregates are used in non-structural uses (e.g. building base course, sub-grade to any car parks and footpaths, backfilling to service trenches, kerb and gutter). If the material cost of new concrete represents less than 1% of the project’s contract value, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Mat - 6 | Steel | To encourage and recognise the reduction in embodied energy and resource depletion associated with reduced use of virgin steel. | Up to two points are awarded as follows: One point is awarded where: 60% of all steel, by mass, in the project either has a post-consumer recycled content greater than 50%, or is reused. Two points are awarded where: 90% of all steel, by mass, in the project either has a post-consumer recycled content greater than 50%, or is reused. If the material cost of steel represents less than 1% of the project’s total contract value, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 2
Mat - 7 | PVC Minimisation | To encourage and recognise the reduction in use of Poly Vinyl Chloride (PVC) products in Australian buildings. | Up to two points are awarded as follows: One point is awarded where: - 30% of the total cost of PVC content was reduced through replacement with alternative materials. Two points are awarded where: - 60% of the total cost of PVC content was reduced through replacement with alternative materials. |  | 2
Mat - 8 | Sustainable Timber | To encourage and recognise the specification of reused timber products or timber that has certified environmentally-responsible forest management practices. | Two points are awarded where 95% (by cost) of all timber products used in the building and construction works have been sourced from any combination of the following: - Reused timber; - Post-consumer recycled timber; or - Forest Stewardship Council (FSC) Certified Timber. If the material cost of timber represents less than 0.1% of the project’s total contract value then this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 2
Mat - 9 | Design for Disassembly | To encourage and recognise designs that minimise the embodied energy and resources associated with demolition. | One point is awarded where: - 50% (by area) of the structural framing, roofing, and façade cladding systems are designed for disassembly. OR - 95% of the total façade is designed for disassembly. If the material cost of the structural framing, roofing, and façade cladding systems represent less than 1% of the project’s total contract value, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Materials Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Mat - 10 | Dematerialisation | To encourage and recognise designs that produce a net reduction in the total amount of material used. | One point is available where a substantial reduction in materials consumption occurs as follows: Where within projects where at least 50% of the GFA is framed in structural steel, and where it is demonstrated that the building’s structural requirements and integrity have been achieved using 20% less steel (by mass) than in a structure with conventional steel framing, without changing the load path to other structural components. OR Where any two of the initiatives below are demonstrated: Structure Within projects where at least 50% of the GFA is framed in structural steel, and where it is demonstrated that the building’s structural requirements and integrity have been achieved using 10% less steel (by mass) than in a structure with conventional steel framing, without changing the load path to other structural components. Ductwork The building is fully naturally ventilated; OR The requirement for ductwork has been reduced by 95%. Building Efficiency For new buildings, where it is demonstrated that Building Efficiency, defined as the ratio of the total NLA over the total GFA, is at least 85%. Finishes As-installed final design must require no finish. 95% of all base building floor material is exposed structure with no covering (e.g. exposed sealed concrete floor); OR 95% of all base building ceiling is exposed structure (and services, where relevant) with no cladding (e.g. exposed concrete ceiling). Cladding 25% of the roof cladding area has a dual function (e.g. roof garden substrate or photovoltaic shingles serve as cladding); OR 25% of the façade cladding area has a dual function (e.g. photovoltaic panels serve as cladding). Piping No piping is used for urinals (i.e. all urinals are waterfree); OR No piping is used for toilets (i.e. all toilets are waterfree); OR Mass of underground piping is reduced by 25% for the same functional requirement and material. |  | 1
|  |  | Total Points = |  | 22 | 0 | 0
Go to Credit Summary

## Land Use & Ecology
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Land Use & Ecology
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Eco - | Conditional Requirement | To encourage and recognise development on land that has limited ecological value and to discourage the development of ecologically valuable sites. | The Eco-Conditional Requirement is met where the project site is not: • On prime agricultural land; should the project site be on prime agricultural land then this project is not eligible for a Green Star certified rating; • On land containing old-growth forest; should the project site be on land containing old-growth forest then this project is not eligible for a Green Star certified rating; • Within 100 metres of a wetland listed as being of ‘high ecological value’. Should the project site be within 100 metres of a wetland listed as being of ‘high ecological value’, then the project can only be deemed eligible for a Green Star certified rating if the project is defined as a ‘refurbishment’ and the Wetland Protection Measures (outlined below) have been completed; • Within 100 metres of a wetland NOT listed as being of high ecological value. Should the project site be within 100 metres of a wetland NOT listed as being of high ecological value, then the project can only be deemed eligible for a Green Star certified rating if the Wetland Protection Measures (outlined below) have been completed. Wetland Protection Measures • A site-specific Wetland Management Plan has been produced, exhibited and implemented; and • All points are achieved in Emi-5 ‘Watercourse Pollution’ and in Emi-7 ‘Light Pollution’. The GBCA reserves the right to provide the final ruling on a project’s compliance with this Conditional Requirement. |  |  | Yes No
Eco - 1 | Topsoil | To encourage and recognise construction practices that preserve the ecological integrity of topsoil. | One point is awarded where: - All topsoil impacted by the construction works is separated and protected from degradation, erosion or mixing with fill or waste; - There is no net change in the volume of topsoil on the site; and - 95% of all topsoil (by volume) retains its productivity. Where no topsoil was impacted by the construction works, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Land Use & Ecology Category Score, type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Eco - 2 | Reuse of Land | To encourage and recognise the reuse of land that has previously been developed. | One point is awarded as follows: If the project is a refurbishment or a building extension; OR If at the time of the site purchase, 75% of the site had been previously built on. |  | 1
Eco - 3 | Reclaimed Contaminated Land | To encourage and recognise developments that reclaim contaminated land that otherwise would not have been developed. | Two points are awarded where: - The site was contaminated at the time of purchase; and - The developer has undertaken full remedial steps to decontaminate the site prior to construction. This credit is ‘Not Applicable’ for projects that are refurbishments or building extensions, and is excluded from the points available used to calculate the Land Use & Ecology Category Score; type "na" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 2
Eco - 4 | Change of Ecological Value | To encourage and recognise developments that maintain or enhance the ecological value of their sites. | Up to four points are awarded where: - For Greenfield sites, the site has no threatened or vulnerable species and for reused sites (e.g. refurbishments), such species are adequately protected if present; - There is no net reduction of native vegetation; and - The ecological value of the site is either not diminished, or is enhanced beyond its previously existing state. The points are determined by the Green Star Change in Ecology Calculator on the basis of comparison between the ‘before’ and the ‘after’ ecological value of the site. |  | 4 | 0
|  |  | Total Points = |  | 8 | 0 | 0
Go to Credit Summary
Go to Change of Ecological Value Calculator

## Ecology Calculator
Green Star - Office Design v3 & Office As Built v3 |  | hidden |  | hidden |  | hidden | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Credit Summary for:
Change In Ecology Calculator | [7 empty] | THESE COLUMNS ARE HIDDEN
| Does the site contain any rare, threatened or vulnerable flora or fauna? | [6 empty] | 1 | 1 | No
[9 empty] | 2 | Yes
In which bio-region is the site located?
|  | Hidden | BEFORE | Hidden | AFTER | Hidden
| Land Type | Ecological Value | Land Types Before Construction / m2 | Ecological Score | Land Types After Construction / m2 | Ecological Score |  | Bioregion Category | Importance Factor |  | Change in ecological diversity index | Credit calculation limits | Credits
| Building | 0 |  | 0 |  | 0 |  | 1 | 0.5 |  | less than -5 | -200 | 0
| Impermeable/concreted Area | 0 |  | 0 |  | 0 |  | 2 | 0.75 |  | -5 to 5 | -5 | 1
| Bare Ground | 5 |  | 0 |  | 0 |  | 3 | 1 |  | 5 to 15 | 5 | 2
| Weed Infestations | 5 |  | 0 |  | 0 |  | 4 | 1.25 |  | 15 to 25 | 15 | 3
| Exotic Garden | 5 |  | 0 |  | 0 |  | 5 | 1.5 |  | above 25 | 25 | 4
| Native Garden | 15 |  | 0 |  | 0
| Exotic Grazing | 5 |  | 0 |  | 0 |  | Bioregion ID = | 2
| Native Grazing* | 20 |  | 0 |  | 0 |  | Category = | 1 |  | Base credits = | 1
| Crop Farming | 5 |  | 0 |  | 0 |  |  |  |  | Threatened species = | 1 | if threatened species then no credits awarded
| Existing Waterway* | 75 |  | 0 |  | 0 |  | Factor = | 0.5 |  | Final credit = | 1
| Wetland* | 100 |  | 0 |  | 0
| Plantation Forest | 10 |  | 0 |  | 0 |  |  |  |  | ERROR Check on Area
| Pine Plantation Forest | 5 |  | 0 |  | 0 |  |  |  |  | If areas don't match then zero credits (default)
| Blue Gum Plantation Forest | 10 |  | 0 |  | 0 |  |  |  |  | CREDIT = | 1
| Regenerated Native Habitat(< 10 years old)* | 50 |  | 0 |  | 0
| Indigenous Native Habitat (> 10 years old)* | 75 |  | 0 |  | 0
| Indigenous Native Habitat (> 20 years old)* | 100 |  | 0 |  | 0
| TOTAL |  | 0 | 0 | 0 | 0
| ECOLOGICAL DIVERSITY INDEX: |  | 0 |  | 0
| CHANGE IN ECOLOGICAL DIVERSITY INDEX |  | 0
| Points Achieved |  | 0
* = affected by Bioregion Reservation Importance Factor
THESE ROWS BELOW ARE HIDDEN
| Name of Bioregion | Bioregion code | Bio-Region ID Number | Ecological Significance Category
| <Don't know> | none | 1 | 5 | Default to highest significance
| Australian Alps | AA | 2 | 1
| Arnhem Coast | ARC | 3 | 4
| Arnhem Plateau | ARP | 4 | 2
| Avon Wheatbelt | AW | 5 | 5
| Brigalow Belt North | BBN | 6 | 5
| Brigalow Belt South | BBS | 7 | 5
| Ben Lomond | BEL | 8 | 3
| Broken Hill Complex | BHC | 9 | 3
| Burt Plain | BRT | 10 | 5
| Central Arnhem | CA | 11 | 4
| Carnarvon | CAR | 12 | 4
| Channel Country | CHC | 13 | 4
| Central Kimberley | CK | 14 | 4
| Central Mackay Coast | CMC | 15 | 3 | check
| Coolgardie | COO | 16 | 3 | check
| Cobar Peneplain | CP | 17 | 4
| Central Ranges | CR | 18 | 5 | check
| Cape York Peninsula | CYP | 19 | 2
| Daly Basin | DAB | 20 | 5
| Darwin Coastal | DAC | 21 | 1
| Desert Uplands | DEU | 22 | 4
| Dampierland | DL | 23 | 5
| Davenport Murchison Ranges | DMR | 24 | 4
| Darling Riverine Plains | DRP | 25 | 5
| Einasleigh Uplands | EIU | 26 | 4
| Esperance Plains | ESP | 27 | 1
| Eyre Yorke Block | EYB | 28 | 3
| Finke | FIN | 29 | 5
| Flinders Lofty Block | FLB | 30 | 4
| Flinders | FLI | 31 | 2
| Gascoyne | GAS | 32 | 4
| Gawler | GAW | 33 | 3
| Gibson Desert | GD | 34 | 2
| Gulf Fall and Uplands | GFU | 35 | 3
| Geraldton Sandplains | GS | 36 | 2
| Great Sandy Desert | GSD | 37 | 4
| Gulf Coastal | GUC | 38 | 5
| Gulf Plains | GUP | 39 | 4
| Great Victoria Desert | GVD | 40 | 1
| Hampton | HAM | 41 | 2
| Jarrah Forest | JF | 42 | 3
| Kanmantoo | KAN | 43 | 3
| King | KIN | 44 | 2
| Little Sandy Desert | LSD | 45 | 4
| MacDonnell Ranges | MAC | 46 | 3
| Mallee | MAL | 47 | 3
| Murray Darling Depression | MDD | 48 | 4
| Mitchell Grass Downs | MGD | 49 | 5
| Mount Isa Inlier | MII | 50 | 4
| Mulga Lands | ML | 51 | 4
| Murchison | MUR | 52 | 5
| Nandewar | NAN | 53 | 5
| Naracoorte Coastal Plain | NCP | 54 | 4
| New England Tableland | NET | 55 | 2
| Northern Kimberley | NK | 56 | 3
| NSW North Coast | NNC | 57 | 1
| NSW South Western Slopes | NSS | 58 | 5
| Nullarbor | NUL | 59 | 3
| Ord Victoria Plain | OVP | 60 | 3
| Pine Creek | PCK | 61 | 1
| Pilbara | PIL | 62 | 4
| Riverina | RIV | 63 | 5
| Sydney Basin | SB | 64 | 1
| South East Coastal Plain | SCP | 65 | 4
| South East Corner | SEC | 66 | 1
| South Eastern Highlands | SEH | 67 | 1
| South Eastern Queensland | SEQ | 68 | 3
| Simpson Strzelecki Dunefields | SSD | 69 | 1
| Stony Plains | STP | 70 | 4
| Sturt Plateau | STU | 71 | 5
| Swan Coastal Plain | SWA | 72 | 3
| Tanami | TAN | 73 | 4
| Tasmanian Central Highlands | TCH | 74 | 2
| Tiwi Cobourg | TIW | 75 | 4
| Tasmanian Northern Midlands | TMI | 76 | 5
| Tasmanian Northern Slopes | TNS | 77 | 3
| Tasmanian South East | TSE | 78 | 4
| Tasmanian Southern Ranges | TSR | 79 | 2
| Tasmanian West | TWE | 80 | 2
| Victoria Bonaparte | VB | 81 | 3
| Victorian Midlands | VM | 82 | 3
| Victorian Volcanic Plain | VVP | 83 | 5
| Warren | WAR | 84 | 1
| Wet Tropics | WT | 85 | 1
| Yalgoo | YAL | 86 | 3
Note on B7: This changes the ecological value of indigenous land types (marked *)
Note on C10: These values are shown in manual
Back to Ecology Credits

## Emissions
Green Star - Office Design v3 & Office As Built v3 |  |  |  | hidden
Credit Summary for:
Emissions
Ref No. | Title | Aim of Credit | Credit Criteria Summary | Related Credits (in other categories) | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Emi - 1 | Refrigerant ODP | To encourage and recognise the selection of refrigerants that do not contribute to long-term damage to the Earth’s stratospheric ozone layer. | One point is awarded where - All HVAC refrigerants have an Ozone Depletion Potential (ODP) of zero OR - No refrigerants are used. |  | 1
Emi - 2 | Refrigerant GWP | To encourage and recognise the selection of refrigerants that reduce the potential for increased global warming from the emission of refrigerants to the atmosphere. | Up to two points are awarded as follows: - One point where 50% of the fluorocarbon refrigerant charge has been replaced with refrigerant(s) that have a Global Warming Potential (GWP) of 10 or less; and - Two points where all refrigerants have a GWP of 10 or less OR where no refrigerants are used at all. |  | 2
Emi - 3 | Refrigerant Leaks | To encourage and recognise building systems design that minimises environmental damage from refrigerant leaks. | Up to two points are awarded as follows: One point is awarded where: - HVAC Systems containing refrigerants are contained in a moderately air tight enclosure; and - A refrigerant leak detection system is installed to cover high-risk parts of the plant. |  | 1
|  |  | An additional point is awarded where: - The point above is achieved; and - The project has installed a refrigerant recovery system that is: - Equipped with an automated pump-down system; and - Sized to effectively and safely capture, isolate, and store 95% (by weight) of the maximum refrigerant charge. Where the project is fully naturally ventilated or is fully mechanically assisted naturally ventilated OR if all points in Emi-1 ‘Refrigerant ODP’ and Emi-2 ‘Refrigerant GWP’ are achieved, this credit is ‘Not Applicable’ and is excluded from the points available used to calculate the Emissions Category Score; type "NA" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Emi - 4 | Insulant ODP | To encourage and recognise the selection of insulants that do not contribute to long-term damage to the Earth’s stratospheric ozone layer. | One point is awarded where no ozone-depleting substances are associated with either the manufacture or the composition of all thermal insulants in the project. |  | 1
Emi - 5 | Watercourse Pollution | To encourage and recognise developments that minimise stormwater run-off to, and the pollution of, the natural watercourses. | Up to three points are awarded as follows: Two points are awarded where: - The development does not increase peak stormwater flows for rainfall events of up to a 1-in 2 year storm; and - All stormwater leaving the site, at any time up to a 1-in-20 year storm event, is treated or filtered in accordance with either: - CSIRO Urban Stormwater: Best Practice Environmental Management Guidelines. OR - Australian and New Zealand Environment Conservation Council (ANZECC)’s Guidelines for Urban Stormwater Management. |  | 2
|  |  | An additional point is awarded where: - The point above is achieved; and - A riparian buffer zone that has three separate zones of pollution buffering is installed within 9 meters of a waterway or natural watercourse and the development. Where the project site does not contain or is not immediately adjacent to a waterway, the additional point is ‘Not Applicable’ and is excluded from the points available used to calculate the Emissions Category Score, type "NA" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Emi - 6 | Discharge to Sewer | To encourage and recognise developments that minimise discharge to the municipal sewerage system. | Up to five points are available as follows: Up to four points are awarded where the building outflows to the sewerage system due to building occupants’ usage have been reduced against an average-practice benchmark as follows: - One point for a 30% reduction; - Two points for a 50% reduction; - Three points for a 70% reduction; and - Four points for a 90% reduction. |  | 4 | 0
|  |  | An additional point is awarded where: - At least one point above was achieved; - There is a Blackwater Treatment Maintenance Plan; and - There is a maintenance contract for a minimum of five year to ensure that the blackwater treatment system operates as intended by the design. Where no blackwater treatment system is installed, the additional point is ‘Not Applicable’ and is excluded from the points available used to calculate the Emissions Category Score: type "NA" in the appropriate 'No. of Points Achieved' column of the rating tool. |  | 1
Emi - 7 | Light Pollution | To encourage and recognise developments that minimise light pollution into the night sky. | One point is awarded where: - No light beam, generated from within the building or outside of the building boundary, is directed at any point in the sky hemisphere without falling directly onto a non-transparent surface; - The lighting design complies with AS4282 “Control of the Obtrusive Effects of Outdoor Lighting”; and - 95% of outdoor spaces do not exceed the minimum requirements of AS1158 for illuminance levels. |  | 1
Emi - 8 | Legionella | To encourage and recognise building systems designed to eliminate the risk of Legionnaire’s disease (Legionellosis) as far as is reasonably practicable. | One point is awarded where: • There are no water based heat rejection system(s) serving the building; OR • Water-based heat rejection system(s) meet all of the following:  -Do not contain water that is kept at a temperature between 20ºC and 50ºC;  -Do not release an aerosol spray during operation;  -Are designed and built to maintain constant movement of the water in the system, when in operation, to prevent stagnation;  -Are designed and built for routine and periodic flushing to remove bio-film buildup and stagnant water from the system(s) whenever it is not in operation; and  -Are designed, located and built in accordance with AS/NZS 3666.1:2002; AND • A Legionella Risk Management plan has been prepared in accordance with AS/NZS 3666.2:2002 or AS/NZS 3666.3:2000 and has been included in the O&M manual provided to the building owner. This credit is applicable to all projects registered after December 18th, 2008. All projects registered prior to this date can choose to use this new credit in its entirety or use the credit issued within the Technical Manual. |  | 1
|  |  | Total Points = |  | 16 | 0 | 0 |  | 0
Go to Credit Summary
Go to Sewerage Calculator

## Sewerage Calculator
Green Star - Office Design v3 & Office As Built v3 |  |  |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Credit Summary for: |  | 0
Sewerage Calculator
| Points Achieved |  | 0
0
WATER CONSUMPTION DUE TO FITTINGS
(from Potable Water Calculator)
The following estimated total potable water consumption is based on the data entered above. The water consumption of the fittings per m2 is based on assumptions of typical office usage and does not represent actual water consumption in the building.
| Predicted Water Consumption from Calculation |  | L/day/m2
0
| WCs |  | 0
| Urinals | #REF! | 0
| Taps | #REF! | 0
| Showerheads | #REF! | 0
SEWERAGE REDUCTION DUE TO RECYCLING
The following estimated total reductions in potable water consumption is based on the data entered above and does not represent actual reduction of water consumption in the building.
| Total Predicted Reduction in Potable Water Consumption |  | L/day/m2
0
| Greywater |  | 0
| Blackwater |  | 0 |  |  | Shower Demand | 0 | <--From Tra-3
| TOTAL REDUCED POTABLE WATER USE |  | L/day/m2
| Predicted Potable Water Consumption from Fixtures calculation |  | 0
| Predicted Recycled Water available to Fixtures |  | 0
| Estimated discharge to sewer (L/day/m2) |  | 0
| Points Achieved |  | 0
| % sewer reduction | Credits | L/day/m2 benchmark |  |  | % sewer reduction | L/day/m2 benchmark ((L/day/person)/(m2/person)) |  |  | Credits | Calc (0%) | Calc (10%) | Calc (15%)
[6 empty] | Shower Demand | No showers installed | Medium Demand (10%) | High Demand (15%) |  | No showers installed | Medium Demand (10%) | High Demand (15%)
| 90% | 4 | 0.1 |  |  |  | 0 | 1 | 2
| 70% | 3 | 0.3 |  |  | 90% | 0.1 | 0.14 | 0.16 | 4 | 1 | 1 | 1
| 50% | 2 | 0.5 |  |  | 70% | 0.3 | 0.42 | 0.48 | 3 | 1 | 1 | 1
| 40% | 1 | 0.6 |  |  | 50% | 0.5 | 0.7 | 0.8 | 2 | 1 | 1 | 1
[6 empty] | 40% | 0.6 | 0.84 | 0.96 | 1 | 1 | 1 | 1
[6 empty] | Benchmark | 1 | 1.4 | 1.6 | 0 | 0 | 0 | 0
[11 empty] | 4 | 4 | 4
[6 empty] | Shower Demand | Description |  | Points Achieved
[6 empty] | 0 | No showers installed |  | 4
[6 empty] | 1 | Tra C-3: 1 credit achieved (or gym provided) |  | 4
[6 empty] | 2 | Tra C-3: 2 credits achieved |  | 4
[6 empty] | TOTAL REDUCED POTABLE WATER USE |  | L/day/m2
[6 empty] | Predicted Potable Water Consumption from Fixtures calculation |  | #REF!
[6 empty] | Predicted Recycled Water available to Fixtures |  | 0
Back to Emissions Credits

## Innovation
Green Star - Office Design v3 & Office As Built v3
Credit Summary for:
Innovation
Ref No. | Title | Aim of Credit | Credit Criteria Summary | No. of Points Available | No. of Points Achieved | Points to be Confirmed | Comments
Inn-1 | Innovative Strategies & Technologies | To encourage and recognise pioneering initiatives in sustainable design, process or advocacy. | Up to two points can be awarded for an innovation initiative where: - The initiative is a technology or process that is considered a ‘first’ in Australia or in the World; OR - The project substantially contributes to the broader market transformation towards sustainable development in Australia or in the World. Points for this credit are allocated as: - One point is awarded when either of the above is true for the Australian market; and - Two points are awarded when either of the above is true for the Global market No individual initiative can achieve more than two points in this credit. Qualifying initiatives may achieve additional points in other Innovation credits, for the maximum of the five points available in total within the Innovation Category. | 2
Inn-2 | Exceeding Green Star Benchmarks | To encourage and recognise projects that achieve environmental benefits in excess of the current Green Star benchmarks. | Up to two points can be awarded for an innovation initiative where there has been a substantial improvement on an existing Green Star credit, as follows: - One point for a solution that results in the elimination of the specific negative environmental impact of the project targeted by an existing credit; and - Two points for a solution that results in a substantial (e.g. 5% or greater above ‘neutral’) restorative environmental impact targeted by an existing credit. No individual initiative can achieve more than two points in this credit. Qualifying initiatives may achieve additional points in other Innovation credits, for the maximum of the five points available in total within the Innovation Category. | 2
Inn-3 | Environmental Design Initiatives | To encourage and recognise sustainable building initiatives that are currently outside of the scope of this Green Star rating tool but which have a substantial or significant environmental benefit. | One point can be awarded where: - An initiative in the project viably addresses a valid environmental concern outside of the current scope of this Green Star tool. No individual initiative can achieve more than one point in this credit. Qualifying initiatives may achieve additional points in other Innovation credits, for the maximum of the five points available in total within the Innovation Category. | 1
|  |  | Total Points = | 5 | 0 | 0 |  | 0
Additional Space for Description of Innovation
Go to Credit Summary

## Credit Summary
Green Star - Office Design v3 & Office As Built v3
Credit Summary for:
Category | Title | Credit No. | Points Available | Points Achieved |  | Points to be Confirmed
Management
| Green Star Accredited Professional | Man-1 | 2 | 0 |  | 0
| Commissioning Clauses | Man-2 | 2 | 0 |  | 0
| Building Tuning | Man-3 | 2 | 0 |  | 0
| Independent Commissioning Agent | Man-4 | 1 | 0 |  | 0
| Building Users' Guide | Man-5 | 1 | 0 |  | 0
| Environmental Management | Man-6 | 2 | 0 |  | 0
| Waste Management | Man-7 | 2 | 0 |  | 0
|  | TOTAL | 12 | 0 |  | 0
Indoor Environment Quality
| Ventilation Rates | IEQ - 1 | 3 | 0 |  | 0
| Air Change Effectiveness | IEQ - 2 | 2 | 0 |  | 0
| Carbon Dioxide Monitoring and Control | IEQ - 3 | 1 | 0 |  | 0
| Daylight | IEQ - 4 | 3 | 0 |  | 0
| Daylight Glare Control | IEQ - 5 | 1 | 0 |  | 0
| High Frequency Ballasts | IEQ - 6 | 1 | 0 |  | 0
| Electric Lighting Levels | IEQ - 7 | 1 | 0 |  | 0
| External Views | IEQ - 8 | 2 | 0 |  | 0
| Thermal Comfort | IEQ - 9 | 2 | 0 |  | 0
| Individual Comfort Control | IEQ - 10 | 2 | 0 |  | 0
| Hazardous Materials | IEQ - 11 | 1 | 0 |  | 0
| Internal Noise Levels | IEQ - 12 | 2 | 0 |  | 0
| Volatile Organic Compounds | IEQ - 13 | 3 | 0 |  | 0
| Formaldehyde Minimisation | IEQ - 14 | 1 | 0 |  | 0
| Mould Prevention | IEQ - 15 | 1 | 0 |  | 0
| Tenant Exhaust Riser | IEQ - 16 | 1 | 0 |  | 0
|  | TOTAL | 27 | 0 |  | 0
Energy
| Conditional Requirement | Ene - | - | - | 0 | 0
| Greenhouse Gas Emissions | Ene - 1 | 20 | 0 |  | 0
| Energy Sub-metering | Ene - 2 | 2 | 0 |  | 0
| Lighting Power Density | Ene - 3 | 3 | 0 |  | 0
| Lighting Zoning | Ene - 4 | 2 | 0 |  | 0
| Peak Energy Demand Reduction | Ene - 5 | 2 | 0 |  | 0
|  | TOTAL | 29 | 0 |  | 0
Transport
| Provision of Car Parking | Tra - 1 | 2 | 0 |  | 0
| Fuel-Efficient Transport | Tra - 2 | 1 | 0 |  | 0
| Cyclist Facilities | Tra - 3 | 3 | 0 |  | 0
| Commuting Mass Transport | Tra - 4 | 5 | 0 |  | 0
|  | TOTAL | 11 | 0 |  | 0
Water
| Occupant Amenity Water | Wat - 1 | 5 | 0 |  | 0
| Water Meters | Wat - 2 | 1 | 0 |  | 0
| Landscape Irrigation | Wat - 3 | 1 | 0 |  | 0
| Heat Rejection Water | Wat - 4 | 4 | 0 |  | 0
| Fire System Water Consumption | Wat - 5 | 1 | 0 |  | 0
|  | TOTAL | 12 | 0 |  | 0
Materials
| Recycling Waste Storage | Mat - 1 | 2 | 0 |  | 0
| Building Reuse | Mat - 2 | 6 | 0 |  | 0
| Reused Materials | Mat - 3 | 1 | 0 |  | 0
| Shell and Core or Integrated Fit-out | Mat - 4 | 2 | 0 |  | 0
| Concrete | Mat - 5 | 3 | 0 |  | 0
| Steel | Mat - 6 | 2 | 0 |  | 0
| PVC Minimisation | Mat - 7 | 2 | 0 |  | 0
| Sustainable Timber | Mat - 8 | 2 | 0 |  | 0
| Design for Disassembly | Mat - 9 | 1 | 0 |  | 0
| Dematerialisation | Mat - 10 | 1 | 0 |  | 0
|  | TOTAL | 22 | 0 |  | 0
Land Use & Ecology
| Conditional Requirement | Eco - | 0 | - | 0 | 0
| Topsoil | Eco - 1 | 1 | 0 |  | 0
| Reuse of Land | Eco - 2 | 1 | 0 |  | 0
| Reclaimed Contaminated Land | Eco - 3 | 2 | 0 |  | 0
| Change of Ecological Value | Eco - 4 | 4 | 0 |  | 0
|  | TOTAL | 8 | 0 |  | 0
Emissions
| Refrigerant ODP | Emi - 1 | 1 | 0 |  | 0
| Refrigerant GWP | Emi - 2 | 2 | 0 |  | 0
| Refrigerant Leaks | Emi - 3 | 2 | 0 |  | 0
| Watercourse Pollution | Emi - 5 | 3 | 0 |  | 0
| Discharge to Sewer | Emi - 6 | 5 | 0 |  | 0
| Light Pollution | Emi - 7 | 1 | 0 |  | 0
| Legionella | Emi - 8 | 1 | 0 |  | 0
| Insulant ODP | Emi - 4 | 1 | 0 |  | 0
|  | TOTAL | 16 | 0 |  | 0
| Sub-total weighted points: | 0 |  |  |  | 0
Innovation
| Innovative Strategies & Technologies | Inn-1 | 2 | 0 |  | 0
| Exceeding Green Star Benchmarks | Inn-2 | 2 | 0 |  | 0
| Environmental Design Initiatives | Inn-3 | 1 | 0 |  | 0
|  | TOTAL | 5 | 0 |  | 0
| Total weighted points: | 0 |  |  |  | 0
Minimal standards for Green Star acreditation not met.
The GBCA does not endorse any self-assessed rating achieved by the use of Green Star - Office V3. The GBCA offers a formal certification process for ratings of Four Stars and above; this service provides for independent third party review of points claimed to ensure all points can be demonstrated to be achieved by the provision of the necessary documentary evidence. The use of Green Star - Office V3 without formal certification by the GBCA does not entitle the user or any other party to promote the Green Star rating achieved.

## Graphical Summary
Green Star - Office Design v3 & Office As Built v3
Summary for:

## Calculation (hidden)
| Green Star - Office v3 |  |  |  |  | New Building
Credit Summary for:
Category Weightings
STATE BASED WEIGHTING FACTORS
| Baseline | ACT | NSW | NT | QLD | SA | TAS | VIC | WA |  | State list
Management | 10% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% |  | 1 | ACT
Indoor Environment Quality | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% |  | 2 | NSW
Energy | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% |  | 3 | NT
Transport | 10% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% |  | 4 | QLD
Water | 15% | 12% | 12% | 10% | 14% | 15% | 10% | 15% | 14% |  | 5 | SA
Materials | 10% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% |  | 6 | TAS
Land use & Ecology | 5% | 6% | 6% | 8% | 4% | 4% | 8% | 4% | 5% |  | 7 | VIC
Emissions | 5% | 6% | 6% | 6% | 6% | 5% | 6% | 5% | 5% |  | 8 | WA
| 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | State selected = | 2 | NSW
note:
[11 empty] | Type of assessment |  |  | Green cells update with changes to Building Input Sheet
[11 empty] | 1 | New Building
[11 empty] | 2 | Refurbished Building
[11 empty] | Type selected = | 1 | New Building
Mandatory requirements
- | 1 | [9 empty] | Type of Rating |  |  |  |  | 1
- | 1 | [9 empty] | 1 |  | Green Star - Office Design v3 & Office As Built v3
[11 empty] | 2 | Green Star - Office Design v3 | Green Star - Office Design v3
| Yes | If there are mandatory requirements then this cell to the left | [8 empty] | 3 | Green Star - Office As Built v3 | Green Star - Office As Built v3
|  | needs to read yes ONLY if they have been met. | [7 empty] | Type Selected = |  | 1 | Green Star - Office Design v3 & Office As Built v3
Points Calculation
| Category | Weighting | Max Score per category | Total of credits available | Credits achieved | % of credits achieved | Weighted Score (achieved) | Credits tbc | % of credits tbc | Weighted Score tbc | Achieved + tbc credits | % of achieved + tbc | Potential weighted score | Error check
| Management | 9% | 9 | 12 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0
| Indoor Environment Quality | 20% | 20 | 27 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0
| Energy | 25% | 25 | 29 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0
| Transport | 8% | 8 | 11 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0
| Water | 12% | 12 | 12 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0
| Materials | 14% | 14 | 22 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0
| Land use & Ecology | 6% | 6 | 8 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0
| Emissions | 6% | 6 | 16 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0
| Total | 100% | 100 | 137 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0
| Innovation |  |  | 5 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0
| Overall Score | [5 empty] | 0 |  |  | 0 | 0 |  | 0 | 0
|  | Scores required for GBRT Ratings |  |  | data for graphical summary page |  |  |  |  | data for graphical summary page
|  | 0 | No Rating |  | Category Score Data |  |  |  |  | Rating Chart | Green Star | Achieved
|  | 10 | One Star | [6 empty] | No Rating | 10 | 0
|  | 20 | Two Star |  |  |  | Achieved | tbc |  | One Star | 10 | 0
|  | 30 | Three Star |  |  | Management | 0% | 0% |  | Two Star | 10 | 0
|  | 45 | Four Star |  |  | Indoor Environment Quality | 0% | 0% |  | Three Star | 15 | 0
|  | 60 | Five Star |  |  | Energy | 0% | 0% |  | Four Star | 15 | 0
|  | 75 | Six Star |  |  | Transport | 0% | 0% |  | Five Star | 15 | 0
| Warning text |  |  |  |  | Water | 0% | 0% |  | Six Stars | 25 | 0
| Error Message = |  |  |  |  | Materials | 0% | 0%
[6 empty] | Land use & Ecology | 0% | 0% |  | Potential |  | 0
| Mandatory Requirements Message |  |  |  |  | Emissions | 0% | 0%
Rating
| Achieved Rating | No Rating |  |  | data for graphical summary page | [5 empty] | data for graphical summary page
| Potential Rating | No Rating |  |  | Credit Graph Data | [5 empty] | Weighted Score Graph Data
| Rating message | [5 empty] | Available | Achieved | tbc |  |  |  | Available | Achieved | tbc
| Minimal standards for Green Star acreditation not met. |  |  |  |  | Management | 12 |  |  |  |  | Management | 9
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | IEQ | 27 |  |  |  |  | IEQ | 20
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Energy | 29 |  |  |  |  | Energy | 25
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Transport | 11 |  |  |  |  | Transport | 8
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Water | 12 |  |  |  |  | Water | 12
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Materials | 22 |  |  |  |  | Materials | 14
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Land use & Ecology | 8 |  |  |  |  | Land use & Ecology | 6
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0
[6 empty] | Emissions | 16 |  |  |  |  | Emissions | 6
[8 empty] | 0 | 0 |  |  |  |  | 0 | 0