## Sheet1
Green Star Rulings
Summary of 2013 rulings released 16th September 2013. Please refer to the Green Star Rulings spreadsheet, available on the GBCA website for all rulings.
Office Interiors v.1.1 | Office v2 | Office v3 | Retail v1 | Education v1 | Healthcare v1 | Industrial v1 | Multi Unit Residential v1 | Credit |  | Ruling Type |  | Ruling text
General
|  | x | [5 empty] | General |  | Technical Clarification | 85 | The Green Star rating tools apply to the entire Green Star project boundary unless otherwise specified within individual credits. In instances where a credit is applicable to a ‘nominated area’, this is defined by the specific credit. The ‘nominated area’ for the following credits is being corrected to apply to BCA Class 5 Net Lettable Area only: - IEQ-1 ‘Ventilation Rates’ - IEQ-2 ‘Air Change Effectiveness’ - IEQ-3 ‘Carbon Dioxide Monitoring & Control’ - IEQ-4 ‘Daylight’ - IEQ-5 ‘Daylight Glare Control’ - IEQ-10 ‘Individual Thermal Comfort Control’ - IEQ-12 ‘Internal Noise Levels’ - IEQ-15 ‘Mould Prevention’ - IEQ-16 ‘Tenant Exhaust Riser’ - Ene-3 ‘Lighting Power Density’ - Ene-4 ‘Lighting Zoning’ - Tra-3 ‘Cyclist Facilities’ - Mat-4 ‘Shell and Core or Integrated Fitout’ Definitions: Class 5 Net Lettable Area: This includes only Class 5 spaces defined as the Net Lettable Area. Please refer to the Property Council of Australia’s ‘Method of Measurement’(2004)
X | X | X | X | X | X | X | X | General |  | Technical Clarification | 86 | Where specifications are required to be submitted as part of credit submissions, either of the following approaches to presenting these specifications is acceptable: 1. Green Star compliant specification clauses are integrated within each individual service’s specifications; OR 2. A Sustainability specification (also called an ESD specification) is developed containing all Green Star and ESD related specification clauses. In order for this to be deemed equivalent, the service’s/ sub-contractor’s specifications must make reference to the ESD Specification and it must be included as an annex or appendix to that specification. Where this approach is adopted, the following must be provided wherever specification extracts are required: - The relevant section of the ESD or Sustainability Specification; and - The section within the relevant services specification referring to the ESD or Sustainability Specification (this reference must quote the actual name of the project's ESD or Sustainability Specification).
[7 empty] | x | General |  | Technical Clarification | 87 | The following clarifications are provided in instances where a multi-unit residential development also includes other uses (for example retail or commercial). The following credits are only applicable to residential spaces (i.e. only apply to BCA Class 1a or Class 2 areas). - IEQ-4 ‘Daylight’ - IEQ-5 ‘Thermal Comfort’ - IEQ-7 ‘Internal Noise Levels’ - IEQ-13 ‘Electric Lighting Levels’ - IEQ-20 ‘Private Outdoor Space’ - IEQ-21 ‘Dwelling Ventilation’ - IEQ-22 ‘Natural Ventilation’ - Ene-Conditional - Ene-1 ‘Greenhouse Gas Emissions’ - Ene-7 ‘Unoccupied Spaces’ - Ene-11 ‘Energy Efficient Appliances’ - Ene-12 ‘Peak Electricity Demand Reduction’ - Tra-1 ‘Provision of Car Parking’ - Tra-2 ‘Fuel Efficient Transport’ - Tra-3 ‘Cyclist Facilities’ - Wat-1 ‘Occupant Amenity Water’ - Wat-7 ‘Water Efficient Appliances’ - Mat-1 ‘Recycling Waste Storage’ - Mat-15 ‘Universal Design’ - Emi-6 ‘Discharge to Sewer’ For all credits not mentioned within this ruling, compliance must be demonstrated for the entire Green Star project site or building in accordance with the detail of each credit.
X | X | X | X | X | X | X | X | General - Commissioning |  | Technical Clarification | 88 | Where documentation calls for *Extract(s) from commissioning report, in place of the requirements as listed in the Technical Manual these extracts must include: - a contents page or chapter headings which confirm that all relevant systems have been included in the commissioning process. - A sign off page demonstrating that the commissioning report and commissioning process has been signed off by all relevant parties including: services engineers, sub-contractors, and the ICA (if an ICA has been engaged) or commissioning manager (if no ICA has been engaged). No further information needs to be provided where commissioning reports are called for.
X | X | X | X | X | X | X | X | General - Commissioning |  | CIR Ruling | 89 | Documentation (As-Built) Where technical manual calls for *Extract(s) From Commissioning Report the project team may instead submit a Certificate of Readiness for all relevant systems. This document must confirm that the relevant systems have been commissioned in line with documented design, commissioning methods used are in line with a relevant commissioning code. This document must be countersigned by the ICA (if engaged) or commissioning manager (if no ICA engaged on project), relevant sub-contractors, relevant services design engineers and the client (or client representative). For a reference certificate of readiness please see CIBSE Guide M Appendix MA4.
Management
x | [7 empty] | Man-2 | Commissioning - Clauses / Tenancy Fitout Commissioning | Correction | 5 | The paragraph below replaces the second last paragraph on page 4 of Man-2 beginning ‘Reference should be made to the importance...’ Whilst it is not required by the referenced standards, project teams are strongly encouraged to consider the implications of commissioning on indoor air quality, for example through establishing an indoor air quality commissioning plan at the design stage with specific provisions for ensuring that this plan is met during and after commissioning. It should be noted that the above: • should be considered as additional advice only. It is additional information to guide project teams in preparing their submissions but does not from part of the credit’s Compliance Requirements. • does not relate to what the required training should include/address. only that which is in the table is relevant to training.
|  |  | x | x | x | x | x | Man-3 | Commissioning - Building Tuning | Correction | 9 | The following services are exempted from the scope of this credit: * Lifts; * Fire services; and * Hydraulic services (wherever greywater and blackwater systems are not present); The following services must be addressed by the credit: * Greywater and blackwater systems. Please refer to the Technical Manual for all compliance and documentation requirements.
X | X | X | X | X | X | X | X | Man-4 | Commissioning - Commissioning Agent | Technical Clarification | 6 | The person or company providing ICA services to a project may change on the following conditions: * Each party is demonstrated to be a 'suitably qualified professional' in line with the compliance requirements of the credit; and * There is a comprehensive handover process between outgoing and incoming ICA. All other requirements outlined with the Technical Manual must be met. To demonstrate the above, the following documentation is required in addition to the documentation requirements outlined within the Technical Manual: * CVs for both ICA parties, in line with the documentation requirements of the credit. * Confirmation from incoming ICA that a handover process took place.
x | x | x | x | x | x | x | x | Man-5/6 | Environmental Management | Documentation (Design) | D | The following is an accepted alternative approach to demonstrating compliance with this credit at the time of a Green Star – Design: In lieu of providing: * Compliance Matrix confirming implementation of the Environmental Management Plan in accordance with Section 3 of the NSW Environmental Management Systems (EMS) Guidelines. Project teams can choose to provide: * The contractor’s accreditation certificate under the NSW EMS Guidelines.
|  | x | x |  | x |  |  | Man-9 | Building Management Systems | Documentation (As Built) | B | Where the facility manager for the project is an in-house employee of the project owner, the following documentation is no longer required at the time of a Green Star – As Built Submission: * Contract with the facilities manager Instead project teams must submit the following: * A letter of commitment from the building owner, which confirms adherence to the same points as the contract requirements outlined in the compliance requirements; and * Extract of facilities manager’s position description outlining the role of the facilities manager which must include the following in line with the requirements of the Credit: - In monitoring energy and water consumption and alarms in the BMS; and - Providing tenants with quarterly reports showing energy and water consumption from each sub-meter.
[7 empty] | X | Man-16 | Metering | Technical Clarification | 5 | For Smart Meters to demonstrate ‘real time’ consumption, they must have the capacity to report metering data every 15 minutes as a minimum. Reporting frequencies of greater than 15 minutes (e.g. Every minute or every 5 minutes) are also deemed compliant.
[7 empty] | X | Man-16 | Metering | Technical Clarification | 6 | The following is deemed to meet the requirement for smart metering for gas: *a pulse meter which shows consumption of gas every 15 minutes (or more frequently) and is connected to a visual display as outlined within the Credit Criteria.
Indoor Environment Quality
|  |  | x |  |  |  |  | IEQ-1 | Ventilation Rates | Correction | 11 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
|  |  | x |  |  |  |  | IEQ-2 | Air Change Effectiveness | Correction | 6 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
X | X | X | X | X | X | X |  | IEQ-2 | Air Change Effectiveness | Documentation (Design) | D | Based on feedback from assessors and project teams, the GBCA is releasing the following documentation approach for IEQ-2 Air Change Effectiveness. This is one acceptable approach to demonstrating compliance with this credit, project teams may choose to demonstrate compliance with the documentation outlined in the Technical Manual if they choose to do so. Documentation Pathway - Design In lieu of all documentation outlined within the Technical Manual (including the CFD Modelling Report), project teams may provide: • A letter from the Mechanical Engineer responsible for design of HVAC systems which (please refer to the template letter available from the GBCA website): - Describes the way in which the HVAC systems have been designed to deliver a uniform distribution of ventilation and to avoid short circuiting of airflow delivery to occupied spaces within the building; and - Explains, in qualitative terms, how the above has been achieved to all occupied spaces. In relation to ventilation of occupied space commentary must cover distribution of supply air diffusers and return air points/paths, location of return air points in relation to supply air, how potential for short circuiting is mitigated, appropriate diffuser selection, supply air temperature and velocity in heating and cooling modes; and - Identifies any spaces that are not mechanically air conditioned and also identifies mechanically air conditioned spaces that do meet the above criteria. -AND- • The CV of the Mechanical Engineer detailing relevant qualifications and experience. Please note that this ruling is an interim solution. The GBCA is currently reviewing and seeking feedback on alternative methods for the assessment of Air Change Effectiveness for Design and As-Built submissions.
X | X | X | X | X | X | X |  | IEQ-2 | Air Change Effectiveness | Documentation (As Built) | E | Based on feedback from assessors and project teams, the GBCA is releasing the following documentation approach for IEQ-2 Air Change Effectiveness. This is one acceptable approach to demonstrating compliance with this credit, project teams may choose to demonstrate compliance with the documentation outlined in the Technical Manual if they choose to do so. Documentation Pathway - As Built In lieu of all documentation outlined within the Technical Manual (including the CFD Modelling Report), project teams may provide: • A letter from a qualified Mechanical Engineer involved in the project during construction and commissioning of HVAC systems which (please refer to the template letter available from the GBCA website): - Describes the way in which the HVAC systems have been designed, constructed and commissioned to deliver a uniform distribution of ventilation and to avoid short circuiting of airflow delivery to occupied spaces within the building; and - Explains, in qualitative terms, how the above has been achieved to all occupied spaces. In relation to ventilation of occupied space commentary must cover distribution of supply air diffusers and return air points/paths, location of return air points in relation to supply air, how potential for short circuiting is mitigated, appropriate diffuser selection, supply air temperature and velocity in heating and cooling modes; and - Identifies any spaces that are not mechanically air conditioned and also identifies mechanically air conditioned spaces that do meet the above criteria; and - Confirms that all relevant systems have been commissioned in line with documented design using a relevant commissioning code (ASHRAE, CIBSE or AIRAH), listing the commissioning code(s) used to guide the commissioning process. -AND- • The CV of the Mechanical Engineer detailing relevant qualifications and experience. Please note that this ruling is an interim solution. The GBCA is currently reviewing and seeking feedback on alternative methods for the assessment of Air Change Effectiveness for Design and As-Built submissions.
|  |  | x |  |  |  |  | IEQ-3 | Carbon Dioxide Monitoring and Control | Correction | 9 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
[7 empty] | x | IEQ-4 | Daylight | Correction | 12 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
x |  | x |  | x |  |  |  | IEQ-3/4 | Daylight | Technical Clarification | 13 | The GBCA has released the 'Green Star Daylight Hand Calculation Guide' which can be used to demonstrate compliance with the Green Star Daylight credit found within this tool. Please refer to the guide for more information.
[6 empty] | x |  | IEQ-11 | Daylight Glare Control | Correction | 20 | The following statement, found within the Compliance Requirements of the credit: The nominated plane must be shown to be shaded from direct sun for 80% of the nominated hours for the winter and spring equinox as well as the summer and winter solstices. Is being corrected to read: The nominated plane must be shown to be shaded from direct sun for 80% of the nominated hours for the spring and autumn equinox as well as the summer and winter solstices.
x | x | x |  | x | x |  |  | IEQ-5/6/12 | High Frequency Ballasts | Documentation | C | Based on feedback from assessors and project teams, the following documentation is no longer required: Design rating: - Short report - Extract(s) from the specification(s) As Built rating: - Short report - As-built drawings - Confirmation from the supplier(s) - Confirmation from the contractor Projects must submit the following documentation instead: - A letter from the project's GSAP confirming compliance with the Credit Criteria.
|  |  | x |  |  |  |  | IEQ-5/9 | Thermal Comfort | Correction | 20 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
| X | X | X | X | X |  |  | IEQ-5/9 | Thermal Comfort | Correction | 21 | Additional Guidance in the IEQ Thermal Comfort credit state that: "Any shading that meets the Credit Criteria of IEQ-5 ‘Daylight Glare Control’ can be included in thermal modelling estimations; all other shading and blinds must be excluded." This wording is corrected to: "All fixed external shading must be included in thermal comfort modelling. There is no need to demonstrate compliance with the Daylight Glare Control credit for these shades to be included in Thermal Comfort modelling. Internal blinds must meet the requirements of IEQ-5 'Daylight Glare Control' to be included in Thermal Comfort modelling."
| X | X | x | x | x | x |  | IEQ-5/9 | Thermal Comfort | CIR Ruling | 22 | Deemed-to-satisfy (DTS) requirement for fully mechanically air conditioned buildings. The following is a deemed to satisfy approach to demonstrating PMV values of between +1 and -1. Thermal modelling is still required to demonstrate PMV values of between +0.5 and -0.5. HVAC requirements: 1. Dry Bulb Temperature in space is controlled to 20°C to 24°C; 2. The HVAC system has separate internal and perimeter zones with independent temperature control which meet the following maximum zone size requirements: 85m2 perimeter zone, 120m2 internal zone for 95% of NLA. 3. Each HVAC zone contains its own temperature sensor(s). Facade requirements: 1. This DTS ruling cannot be applied to a refurbishment project that reuses any portion of existing facade. It can only be used if the entire building fabric is new. Please contact the GBCA if you would like to use a modified version of this ruling for a refurbishment project. Documentation requirements At the time of a Green Star - Design submission, please provide the following: • Short report summarising how each of the above criteria have been met, referencing supporting information. • Extracts from the mechanical specifications showing the clauses demonstrating the above mechanical criteria have been met • Marked up Tender Mechanical Drawings demonstrating mechanical zoning criteria listed above have been met. No further documentation is required. At the time of a Green Star - As Built submission, please provide the following: • Short report summarising how each of the above criteria have been met, referencing supporting information. • Confirmation from the relevant sub-contractors that all services have been installed and commissioned in line with the above listed criteria • Marked up As-Built Mechanical Drawings demonstrating mechanical zoning criteria listed above have been met. No further documentation is required.
[7 empty] | x | IEQ-5/9 | Thermal Comfort | Documentation | B | Where one point is being claimed for providing ceiling fans for at least 95% of all apartments, please submit the following evidence and ensure it readily confirms compliance: Design rating: - Short Report prepared by a suitable professional that describes how the Credit Criteria has been met by including a calculation indicating the number of apartments with ceiling fans specified as a percentage of the total number apartments; - Tender Drawings clearly marked up indicating the location of ceilings fans to be installed within the specified apartments. As Built rating: - Short Report prepared by a suitable professional that describes how the Credit Criteria has been met by including a calculation indicating the number of apartments with ceiling fans installed as a percentage of the total number apartments; - As Built Drawings clearly marked up indicating the location of ceilings fans that have been installed within the specified apartments. Where 2 points are being claimed, all documentation as per the Technical Manual must be submitted for assessment.
x | [7 empty] | IEQ-6/9/11 | Asbestos | Documentation (Design & As Built) | C | The credit is automatically recognised as being 'not applicable', where the fitout is located within a Green Star Office - Design or As Built certified building that was awarded 'not applicable'. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related certified project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
|  |  | x |  |  |  |  | IEQ-7/10/12 | Internal Noise Levels | Correction | 15 | The following Credit Criteria for claiming the credit as 'Not Applicable' has been withdrawn. If 'open air mall' areas make up more than 95% of the project's total common areas, this credit is 'Not Applicable' and is excluded from the points available used to calculate the Indoor Environment Quality Category Score.
[7 empty] | x | IEQ-7/10/12 | Internal Noise Levels | Documentation (Design) | C | The following documentation is no longer required at the time of a Green Star – Design submission for this credit: • Manufacturer’s data sheet detailing the acoustic properties of the material used in the wall, ceiling floor construction.
|  |  |  | x | x |  |  | IEQ-9/12/14 | Formaldehyde Minimisation | Technical Clarification | 30 | The GBCA confirms that the scope of this credit includes all fitout items, including loose furniture.
[5 empty] | x |  |  | IEQ-17 | Air Distribution Systems / Air Supply Ductwork | Documentation (As Built) | C | Based on feedback from the assessors and project teams, the following documentation is no longer required at the time of a Green Star – As-Built submission for this credit: * Extract from the specifications(s) Instead of Extracts from the specification(s) project teams must submit the following: * Extract(s) from the Commissioning Report showing: - The humidity levels in the ducts and in the occupied space for all modes of operation; and - That the testing occurred using the range stated in the control system and demonstrate that all valves, dampers, fans, and the rest of the equipment, work as intended. All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x | IEQ-20 | Private External Space | Correction | 3 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
[7 empty] | x | IEQ-21 | Dwelling Ventilation | Correction | 2 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
[7 empty] | x | IEQ-22 | Natural Ventilation | Correction | 1 | The following statement, found within the Compliance Requirements of the credit: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries, with a ventilation opening; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. Is being corrected to read: For the purposes of this credit, 'living area' is defined as the total floor area of the dwelling excluding; - Floor area that is not fully enclosed; - Bathrooms, ensuites and laundries; and - Voids, store rooms, garages and car parks. Built-in and walk-in wardrobes are considered to be store rooms for the purpose of this Green Star credit. i.e. bathrooms, ensuites and laundries are excluded regardless of the presence of ventilation openings.
Energy
x | x | x | x | x | x | x | x | Ene-0 | General | Technical Clarification | 3 | All modelling of PV systems must be carried out in line with the "Green Star - Photovoltaic Modelling Guidelines" available on the GBCA website.
X | X | X |  | X | X | X |  | Ene-4/6 | Lighting Zoning | Technical Clarification | 10 | Where projects have installed an addressable lighting control system, the following must be shown in the documentation provided: - Drawings with all soft switches identified and highlighted, including an electrical services legend identifying symbols used. (Soft switch - an addressable switching mechanism such as a light level detector, motion detector or light switch, which is connected to an addressable lighting control system). - A statement from the electrical or lighting designers or contractor that no zone exceeds 100m2 for 95% of the tenancy. - Ensure the drawings provided represent each typical floor or lighting layout; and where lighting layouts differ between floors, drawings for each floor must be provided.
Water
| x | x | x | x | x |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Correction | 31 | The 'Potable Water Calculator Guide' referred to in the Compliance Requirements is not available. Project teams must comply with all requirements outlined in the Technical Manual.
|  |  | x | x |  |  |  | Wat-1 | Occupant Amenity Potable Water Efficiency / Potable Water Efficiency | Documentation (As Built) | C | In a Green Star – As Built submission for this credit, in place of the following documentation: • Confirmation(s) from the supplier(s); and • Confirmation from the contractor. It is acceptable to submit the following: • As Built Fixtures and Fitting Schedule - listing and describing all hydraulic fixtures and fittings in the project and their flow rates. In a Green Star – As Built submission for this credit, where no rainwater collection or water reuse systems are present or no automatic controls are present, the following documentation is NOT required: • As built hydraulic schematic drawings - showing the location of all water reuse, collection and storage systems. All other documentation requirements not mentioned here remain applicable.
|  | x | x | x | x | x | x | Wat-3 | Landscape Irrigation | Documentation | C | Where the project team is claiming that 100% of irrigation water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. As such, the documentation requirements have been amended as follows: Short Report by a suitably qualified engineer detailing: • The proposed landscape irrigation system and its water sources and operation; • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection). • Reference to how each of the demands is connected to the non-potable water supply; • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water; and • Referencing the hydraulics drawings (Tender or As Built dependent on the certification sought) and the extracts from specifications (Design submission) or commissioning report (As Built submission). All other documentation requirements not mentioned here remain applicable.
|  | x | x | x | x |  | x | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation | D | Where the project team is claiming that 100% of heat rejection water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. As such, the documentation requirements have been amended as follows: In the Short Report, in lieu of: • Providing calculations (and justifying the values used) for the reference case; and • Demonstrating how the proposed system meets the credit criteria against the reference case. The following must be included: • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection) the calculation for cooling demand must reflect the thermal model used for Ene-1 Greenhouse Gas Emissions with specific refernce to peak events. • Reference to how each of the demands is connected to the non-potable water supply; and • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water. All other documentation requirements not mentioned here remain applicable.
[6 empty] | x |  | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation | E | Where the project team is claiming that 100% of heat rejection water demands are met by non-potable water, there is no requirement to establish a reference case as outlined in the compliance requirements of the credit. In the Short Report, in lieu of the information required for a reference case (text highlighted red): • Where water-based heat rejection system(s) are present, detailing any heat rejection system(s) in the project; providing calculations and justifying the values used; and describing how the proposed system meets the credit criteria against the reference case with specific reference to peak events. The following must be included: • Calculations to determine the amount of non-potable water (rainwater and recycled/reclaimed (both the onsite and offsite supply)) available on a monthly basis by referencing drawings, specifications and confirmation of recycled water supply. Where off-site recycled/reclaimed water is used to reduce potable water consumption, it must be demonstrated that the relevant local authority has given approval for the project's use of this water. • Calculations to determine the demand from all uses in the project that will use non-potable water (taps, WCs, urinals, showers, Landscape Irrigation, and Heat Rejection). • Reference to how each of the demands is connected to the non-potable water supply; and • A summary table demonstrating that there is sufficient non-potable water supply to meet 100% of the requirements for each use against the total available non-potable water. All other documentation requirements not mentioned here remain applicable.
|  | x | x | x |  |  |  | Wat-4 | Cooling Tower Water Consumption/Heat Rejection Water | Documentation (As Built) | F | For mechanically air-conditioned spaces, projects may provide, in place of the As Built hydraulic drawings, other As Built drawings, such as mechanical drawings, provided that the information requested in the Technical Manual has been included.
|  |  |  | x |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Correction | 1 | The Documentation Guidelines - Design as detailed in the Technical Manual are withdrawn and replaced by: Documentation Guidelines - Design Submit all the evidence and ensure it readily confirms compliance. o Short report o Extract(s) of the specification(s) o Tender schematic hydraulic drawings If the credit is claimed due to there being no once-through cooling system installed o Short report Where the credit is claimed as ‘Not Applicable’: o Confirmation from the architect o Tender drawings Short report by a suitably qualified hydraulic engineer: • Detailing the proposed laboratory equipment for cooling, it's water sources and operation; • Demonstrating how the proposed system meets the Credit Criteria; and • Referencing specification extract(s) and tender schematic hydraulic drawings when necessary. If there is no once-through cooling: • Demonstrating that no once-through cooling systems are installed. Extract(s) from the specification(s) identifying the proposed water-using equipment, its water sources and operation requirements. Tender schematic hydraulic drawings indicating the design, location and water supply of the equipment cooling system. Confirmation from the architect referencing the tender drawings; • That less the 10% of the buildings nominated area is devoted to laboratories; OR • That no laboratories are included in the building. Tender drawings showing the use of each area within the buildings and clearly indicating the percentage of laboratories within the project.
|  |  |  | x |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Correction | 2 | The Documentation Guidelines - As Built as detailed in the Technical Manual are withdrawn and replaced by: Documentation Guidelines - As Built Submit all the evidence and ensure it readily confirms compliance. o Short report o Extract(s) from the Commissioning Report o As Built hydraulic drawings If the credit is claimed due to there being no once-through cooling system installed o Short report Where the credit is claimed as ‘Not Applicable’: o Confirmation from the architect o As Built drawings Short report by a suitably qualified hydraulic engineer: • Detailing the proposed laboratory equipment for cooling, it's water sources and operation; • Demonstrating how the proposed system meets the Credit Criteria; and • Referencing the As Built hydraulic drawings and the Commissioning Report extracts when necessary. If there is no once-through cooling: • Demonstrating that no once-through cooling systems are installed. Extract(s) from the Commissioning Report demonstrating that the system has been commissioned and operates as intended by the design, and as expressed in the hydraulics report. As Built hydraulic drawings indicating the design, location and water supply of the laboratory equipment cooling system. Confirmation from the architect referencing the As Built drawings; • That less the 10% of the buildings nominated area is devoted to laboratories; OR • That no laboratories are included in the building. As Built drawings showing the use of each area within the buildings and clearly indicating the percentage of laboratories within the project.
|  |  |  | x |  |  |  | Wat-6 | Potable Water Use in Laboratories/Equipment | Technical Clarification | 3 | For As Built projects For projects where the design of the building has not changed, and the total area of laboraties present within the building has not changed then this credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet and include a note stating that the building design has not changed. Where this approach is adopted, no further documentation is required for this credit. If the building areas have changed, or the area of laboratory has increased, then full documentation in compliance with the Technical Manual must be provided.
Materials
x | [7 empty] | Mat-1 | Recycling Waste Storage | CIR Ruling | 15 | Projects may use the following rates for the provision of recycling storage space: • 1m2 per 12 workstations where there is a fortnightly collection service in place; • 1m2 per 24 workstations where there is a weekly collection service in place; and • 1m2 per 120 workstations where there is a daily recycling collection service in place. All documentation must be submitted as per the Compliance Requirements.
|  | x | x | x | x | x | x | Mat-2 | Building Re-use | Documentation (As Built) | F | The credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x | Mat-5/6 | Steel (April 2010) | Technical Clarification | 9 | Reinforcing steel includes reinforcing bar and mesh used in concrete reinforcement in the building structure. This includes steel in situ, stressed, and pre-cast concrete applications. For the purposes of this credit post tensioning tendons are not considered to be reinforcing steel and are therefore excluded from the scope of this credit.
|  | x | x | x | x | x | x | Mat-9 | Design for Disassembly | Technical Clarification | 9 | The Credit Criteria for 95% of the total façade to be designed for disassembly only applies to new components of a building. For refurbishments, the percentage must be calculated from new elements only (including new elements attached to existing façade); for the purpose of this credit, previously existing elements may be excluded from the total area.
[7 empty] | x | Mat-9/10 | Dematerialisation | Technical Clarification | 6 | Where this credit refers to a ‘prefabricated module’ in relation to kitchens and bathrooms this must be interpreted as a kitchen or bathroom module, which is entirely ready-made offsite and positioned in the apartment and then connected to services. It does not mean a ‘modular’ kitchen or bathroom which is brought into the apartment in pieces and assembled onsite.
[7 empty] | x | Mat-14 | Internal Walls | Documentation (As Built) | B | Based on feedback from assessors and project teams, the following documentation is no longer required at the time of a Green Star – As Built submission for this credit. *Access Review Report *Short Report dot point 3: ‘Demonstrating that all publicly accessible areas and at least 10% of dwellings have been designed to comply with class A, B or C requirements of AS4299-1995. Projects must submit the following documentation instead: *Copy of the Internal Walls Calculator completed for the project and referencing supporting documentation *Short Report presented by a suitable professional that describes how Credit Criteria have been met by: o Summarising how the nominated internal walls meet the credit criteria o Listing and referencing all the nominated internal walls in the project; and o Nominating which assessment categories in the calculator have been achieved by the internal walls. This must clearly correlate with the ‘confirmation from the supplier(s)’ and the ‘manufacturer documentation’. All other documentation must be provided as per the Technical Manual at the time of submission.
[7 empty] | x | Mat-15 | Universal Design | CIR Ruling | 1 | Projects that provide at least 10% of dwellings that meet the Platinum Level of the Livable Housing Design Guidelines are deemed to meet the requirements for one point in this credit. Please refer to Documentation (Design) A and Documentation (As Built) B for documentation requirements which must be adhered to when adopting this approach.
[7 empty] | x | Mat-15 | Universal Design | Documentation (Design) | A | To be used in conjuction with Mat-15 CIR Ruling 1 only. Submit all the evidence and ensure it readily confirms compliance. • Provisional Livable Housing Design Certificates -OR- • Short report • Tender drawing(s) • Extract(s) from the specifications Copies of the Platinum Level Provisional Livable Housing Design Certificates (issued for the design of dwellings) for at least 10% of dwellings issued by Livable Housing Australia. Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: • Referencing supporting documentation and describing, with calculations and summary tables wherever appropriate, how the Credit Criteria have been achieved; and • Demonstrating that at least 10% of dwellings have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. Tender drawing(s) marked up to show the features which have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. Extract(s) from the specifications demonstrating how the dwellings comply with the Platinum Level requirements of the Livable Housing Design Guidelines.
[7 empty] | x | Mat-15 | Universal Design | Documentation (As Built) | B | To be used in conjuction with Mat-15 CIR Ruling 1 only. Submit all the evidence and ensure it readily confirms compliance. • Final Livable Housing Design Certificates -OR- • Short report • As-built drawing(s) Copies of the Platinum Level Final Livable Housing Design Certificates (issued for the constructed dwellings) for at least 10% of dwellings issued by Livable Housing Australia. Short report prepared by a suitable professional that describes how the Credit Criteria have been met by: • Referencing supporting documentation and describing, with calculations and summary tables wherever appropriate, how the Credit Criteria have been achieved; and • Demonstrating that at least 10% of dwellings have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines. As-built drawing(s) marked up to show the features that have been designed to comply with the Platinum Level requirements of the Livable Housing Design Guidelines.
Land Use and Ecology
| x |  | x | x | x | x |  | Eco-1/5 | Topsoil / Topsoil and Fill Removal | Documentation (As Built) | B | For As Built projects The following simplified documentation pathway is available for projects which were awarded this credit as being 'not applicable' to their project at the Design stage for either of the following reasons: 1. The project is refurbishment; or 2. The topsoil on site is inherently non-productive. Projects which wish to claim this credit as being 'not applicable' because no topsoil was impacted by the construction works must provide documentation as per the Technical Manual to be assessed at the As Built stage. This credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage (as outlined above). To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x |  | x | x | x | x |  | Eco-2 | Reuse of Land | Documentation (As Built) | C | For As Built projects Points for this credit are automatically awarded, following the successful award of points at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
| x | x | x | x | x | x | x | Eco-3 | Reclaimed Contaminated Land | Documentation (As Built) | C | For As Built projects This credit is automatically recognised as being 'not applicable', following the successful award of 'na' at the Design stage. To demonstrate compliance, the project team must: - Include the final results spreadsheet for the related Design project in the General Section of the submission; - Reference this ruling on the Credit Cover sheet Where this approach is adopted, no further documentation is required for this credit.
|  | x | x | x | x | x | x | Eco-4 | Change of Ecological Value | Correction | 4 | The following Credit Criteria replaces that found within the Technical Manual for this credit: Where the threatened species requirement has been met, up to four points are awarded where as a result of the development, the ecological value of the site is either maintained or enhanced. The number of points awarded is determined by the Green Star - Change of Ecological Value Calculator based on a comparison of the state of the site before and after design/construction. Threatened species requirement: For Greenfield sites, the site has no threatened or vulnerable species and for reused sites (e.g. refurbishments), such species are adequately protected if present. Please refer to the Technical Manual, and previous rulings, for Documentation and Compliance Requirements.
x | [7 empty] | Eco-3 | Building Environmental Management | CIR Ruling | 4 | It is acceptable to provide evidence of the implementation of the environmental initiatives rewarded by this credit with the following types of documentation (in lieu of the documentation stipulated within the Technical Manual): • A contract between the tenant and the building management. The contract must require the landlord/ building manager to implement, manage and report on at least two environmental initiatives per the Credit Criteria and Additional Guidance. There is no requirement for this contract to contain penalty clauses. -OR- • An executed, countersigned, letter. The letter must detail the requirement of the building management to implement, manage and report on at least two environmental initiatives per the Credit Criteria and Additional Guidance. Where the project team pursues this through an executed counter signed letter, the letter must address the following: • Be addressed to one of the relevant parties (and written by the other); and • Be signed by both parties. Please note, there is no requirement for this executed letter agreement to contain penalty clauses.
x | [7 empty] | Eco-3 | Building Environmental Management | Correction | 5 | Regardless of the approach used to demonstrate compliance with the credit, be it through a contract, lease or executed letter, there is no requirement to demonstrate the presence of penalty clauses.
x | [7 empty] | Eco-4 | Commitment to Building Performance | CIR Ruling | 3 | Project teams may to provide evidence of the implementation of the environmental initiatives rewarded by this credit with the following types of documentation (in lieu of the documentation stipulated within the Technical Manual): • An executed, countersigned, letter. The letter must detail the tenants requirement to comply with the building management's environmental initiatives per the Credit Criteria and Additional Guidance. Where the project team pursues this through an executed or counter-signed letter, the letter must address the following: • Be addressed to one of the relevant parties (and written by the other); and • Be signed by both parties. Please note, there is no requirement for this executed letter agreement to contain penalty clauses.
x | [7 empty] | Eco-4 | Commitment to Building Performance | Correction | 4 | Regardless of the approach used to demonstrate compliance with the credit, be it through a contract, lease or executed letter, there is no requirement to demonstrate the presence of penalty clauses.
Emissions
x | x | x | x | x | x | x | x | Emi-1 | Refrigerant ODP | Technical Clarification | 2 | If all refrigerants on a project are Zero ODP then no information needs to be provided to state or confirm the volume of refrigerants. Please refer to the Technical Manual and Documentation rulings for all documentation requirements, this ruling does not impact on the type or number of documents which are required to be provided for this credit (only the content).
x | x | x | x | x | x |  | x | Emi-1 | Refrigerant ODP | Documentation (As Built) | C | Based on feedback from assessors and project teams the following documentation is no longer required for Green Star (As-Built Submissions): *Confirmation from contractor *Extracts from the commissioning report
x | x | x | x | x | x | x | x | Emi-1 | Refrigerant ODP | Documentation (As Built) | D | The following refrigerants are acknowledged as being Zero ODP: R-134a, R-125, R404A, R407B, R407C, R-410A, R-413A, R-507, HC-290, HC-600, HC-600a, R-717, R-744, R-1270. As such, wherever these refrigerants are used there is no requirement for the confirmation from the suppliers to include evidence that the refrigeratns have an ODP of zero. All other evidence must be provided as per the Technical Manual and other rulings. Please refer to the Technical Manual and rulings for all other documentation requirements, this ruling removes the requirement to provide documentation confirming the ODP of the above listed refrigerants only.
x | x | x | x | x | x | x | x | Emi-2/4/9 | Insulant ODP | Documentation | B | Based on feedback from assessors and project teams, the following documentation is no longer required: Design rating: - Extract(s) from the specification(s) As Built rating: - Confirmation from the supplier(s) - Confirmation from the contractor Projects (both Design and As Built) must submit the following documentation instead: - A letter from the project's GSAP confirming compliance with the Credit Criteria.
| x | x | x | x | x | x | x | Emi-8 | Legionella / Cooling Towers | Technical Clarification | 2 | This credit is limited to water based heat rejection systems. Evaporative coolers which cool air within the building, and do not form part of the heat rejection system for the buidling's HVAC, are not considered water based heat rejection systems for the purposed of this credit. Projects which only contain evaporative cooling systems can target points for this credit by providing the documentation outlined for ‘where there are no water-based heat rejection system serving the building(s)’.
| x | x | x | x | x | x | x | Emi-8 | Legionella / Cooling Towers | Technical Clarification | 3 | The GBCA confirms that combination wet/dry heat rejection systems which are combination of air-cooled chillers and evaporative cooling systems are to be treated as 'water based heat rejection systems' and documented within this credit accordingly. If the selected systems comply with the credit criteria for water based systems, then it will be possible to target a point for this credit using that compliance pathway. Please refer to the credit for all documentation and compliance requirements.